## Solar PV system data
This spreadsheet is designed to give an estimation on the impact of the installation of Solar PV generation at a site alongside the installation of electric vehicles. It is not necessary to use the tool where solar generation is already installed and is included in the background load metering. Users can enter their site's existing background load, together with details of their proposed PV system in order to output a load profile adjusted for EV charging.
Please note that this tool provides an estimation only. Output of solar generation may vary and this should be considered when sizing network connection requests.
| MPAN | S000000000001
| Site Name | Name
| Location | Location
| Solar PV system (kWp) | 100
| DNO Region | (10) UKPN - Eastern England
| Irradiation (kW/m2) | 1267
| Yield (kWh/kWp) | 1076.95
| Yearly solar production (kWh) | 107695
| Consumption (kWh) ex solar | 0
| Consumption (kWh) with solar | -107695
| Instructions | The cells/sheets marked in yellow must be updated
1 | Enter the site's MPAN in cell C6
2 | Optionally, enter the site name and location in cells C7 and C8 for easy identification
3 | Enter the proposed size of the PV generation system in cell C9 in kWp
4 | Select your DNO Region in cell C10
5 | On the page "Consumption (kWh) ex solar", enter your half-hourly meter data in local time. Ensure that the days of the year align with the days in column A, and that the dates in this column are updated to the correct year (2001 is the default). Using a full year of data is preferred but not necessary. If your data includes a leap year, remove the line for 29 February before entering into the sheet. Do not include extra hours, or leave missing hours for daylight saving changes (if necessary, fill the gap with data from the adjacent hours).
6 | Your total solar generation and consumption will appear in the table above, and in half-hourly form in the tab 'Consumption (kWh) with solar'
7 | To output your file for use in the Site Planning Tool, go to 'Consumption (kWh) with solar' then File… Save As…. Enter a name for the file and choose the file type 'CSV Comma Delimited (*.csv)'. Save, and select OK on the dialog box that appears.
8 | The file can now be uploaded to the Site Planning Tool. If you have not entered a full year of load data, first ensure you delete any rows/days for which data was not provided.
Assumptions
In order to provide an estimation of Solar PV load the following assumptions are made by this tool:
1 | Hours of sunlight are based on a six-year average for a central London location sourced from the European Commission's PVGIS database, adjusted for daylight savings time. Actual hours of sunlight may vary slightly based on location.
2 | Solar irradiation is based on a representative location within each DNO region. Solar irradiation can vary due to local landscape and if needed the 'Yearly in-plane irradiation [kWh/m2]' for a location can be taken from https://re.jrc.ec.europa.eu/pvg_tools/en/ and used to replace the number in cell C11 for a more accurate result.
3 | A loss of 15% is applied to the system output.
4 | Figures are based on a fixed crystalline silicon PV system on a 30˚ slope at 0˚ Azimuth.
5 | Output site load for each half hour is a minimum of 0kW as the Site Planning Tool will not calculate using negative background loads/show feed-in to the grid.
The next step is to enter the site data into the Site Planning Tool:
The site planning tool can be found at www.optimise-prime.com/site-planning-tool
Site Planning Tool
Solar Power Estimator

## Consumption (kWh) ex solar
Date | 0:00 | 0:30 | 1:00 | 1:30 | 2:00 | 2:30 | 3:00 | 3:30 | 4:00 | 4:30 | 5:00 | 5:30 | 6:00 | 6:30 | 7:00 | 7:30 | 8:00 | 8:30 | 9:00 | 9:30 | 10:00 | 10:30 | 11:00 | 11:30 | 12:00 | 12:30 | 13:00 | 13:30 | 14:00 | 14:30 | 15:00 | 15:30 | 16:00 | 16:30 | 17:00 | 17:30 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 20:30 | 21:00 | 21:30 | 22:00 | 22:30 | 23:00 | 23:30
2021-01-01
2021-01-02
2021-01-03
2021-01-04
2021-01-05
2021-01-06
2021-01-07
2021-01-08
2021-01-09
2021-01-10
2021-01-11
2021-01-12
2021-01-13
2021-01-14
2021-01-15
2021-01-16
2021-01-17
2021-01-18
2021-01-19
2021-01-20
2021-01-21
2021-01-22
2021-01-23
2021-01-24
2021-01-25
2021-01-26
2021-01-27
2021-01-28
2021-01-29
2021-01-30
2021-01-31
2021-02-01
2021-02-02
2021-02-03
2021-02-04
2021-02-05
2021-02-06
2021-02-07
2021-02-08
2021-02-09
2021-02-10
2021-02-11
2021-02-12
2021-02-13
2021-02-14
2021-02-15
2021-02-16
2021-02-17
2021-02-18
2021-02-19
2021-02-20
2021-02-21
2021-02-22
2021-02-23
2021-02-24
2021-02-25
2021-02-26
2021-02-27
2021-02-28
2021-03-01
2021-03-02
2021-03-03
2021-03-04
2021-03-05
2021-03-06
2021-03-07
2021-03-08
2021-03-09
2021-03-10
2021-03-11
2021-03-12
2021-03-13
2021-03-14
2021-03-15
2021-03-16
2021-03-17
2021-03-18
2021-03-19
2021-03-20
2021-03-21
2021-03-22
2021-03-23
2021-03-24
2021-03-25
2021-03-26
2021-03-27
2021-03-28
2021-03-29
2021-03-30
2021-03-31
2021-04-01
2021-04-02
2021-04-03
2021-04-04
2021-04-05
2021-04-06
2021-04-07
2021-04-08
2021-04-09
2021-04-10
2021-04-11
2021-04-12
2021-04-13
2021-04-14
2021-04-15
2021-04-16
2021-04-17
2021-04-18
2021-04-19
2021-04-20
2021-04-21
2021-04-22
2021-04-23
2021-04-24
2021-04-25
2021-04-26
2021-04-27
2021-04-28
2021-04-29
2021-04-30
2021-05-01
2021-05-02
2021-05-03
2021-05-04
2021-05-05
2021-05-06
2021-05-07
2021-05-08
2021-05-09
2021-05-10
2021-05-11
2021-05-12
2021-05-13
2021-05-14
2021-05-15
2021-05-16
2021-05-17
2021-05-18
2021-05-19
2021-05-20
2021-05-21
2021-05-22
2021-05-23
2021-05-24
2021-05-25
2021-05-26
2021-05-27
2021-05-28
2021-05-29
2021-05-30
2021-05-31
2021-06-01
2021-06-02
2021-06-03
2021-06-04
2021-06-05
2021-06-06
2021-06-07
2021-06-08
2021-06-09
2021-06-10
2021-06-11
2021-06-12
2021-06-13
2021-06-14
2021-06-15
2021-06-16
2021-06-17
2021-06-18
2021-06-19
2021-06-20
2021-06-21
2021-06-22
2021-06-23
2021-06-24
2021-06-25
2021-06-26
2021-06-27
2021-06-28
2021-06-29
2021-06-30
2021-07-01
2021-07-02
2021-07-03
2021-07-04
2021-07-05
2021-07-06
2021-07-07
2021-07-08
2021-07-09
2021-07-10
2021-07-11
2021-07-12
2021-07-13
2021-07-14
2021-07-15
2021-07-16
2021-07-17
2021-07-18
2021-07-19
2021-07-20
2021-07-21
2021-07-22
2021-07-23
2021-07-24
2021-07-25
2021-07-26
2021-07-27
2021-07-28
2021-07-29
2021-07-30
2021-07-31
2021-08-01
2021-08-02
2021-08-03
2021-08-04
2021-08-05
2021-08-06
2021-08-07
2021-08-08
2021-08-09
2021-08-10
2021-08-11
2021-08-12
2021-08-13
2021-08-14
2021-08-15
2021-08-16
2021-08-17
2021-08-18
2021-08-19
2021-08-20
2021-08-21
2021-08-22
2021-08-23
2021-08-24
2021-08-25
2021-08-26
2021-08-27
2021-08-28
2021-08-29
2021-08-30
2021-08-31
2021-09-01
2021-09-02
2021-09-03
2021-09-04
2021-09-05
2021-09-06
2021-09-07
2021-09-08
2021-09-09
2021-09-10
2021-09-11
2021-09-12
2021-09-13
2021-09-14
2021-09-15
2021-09-16
2021-09-17
2021-09-18
2021-09-19
2021-09-20
2021-09-21
2021-09-22
2021-09-23
2021-09-24
2021-09-25
2021-09-26
2021-09-27
2021-09-28
2021-09-29
2021-09-30
2021-10-01
2021-10-02
2021-10-03
2021-10-04
2021-10-05
2021-10-06
2021-10-07
2021-10-08
2021-10-09
2021-10-10
2021-10-11
2021-10-12
2021-10-13
2021-10-14
2021-10-15
2021-10-16
2021-10-17
2021-10-18
2021-10-19
2021-10-20
2021-10-21
2021-10-22
2021-10-23
2021-10-24
2021-10-25
2021-10-26
2021-10-27
2021-10-28
2021-10-29
2021-10-30
2021-10-31
2021-11-01
2021-11-02
2021-11-03
2021-11-04
2021-11-05
2021-11-06
2021-11-07
2021-11-08
2021-11-09
2021-11-10
2021-11-11
2021-11-12
2021-11-13
2021-11-14
2021-11-15
2021-11-16
2021-11-17
2021-11-18
2021-11-19
2021-11-20
2021-11-21
2021-11-22
2021-11-23
2021-11-24
2021-11-25
2021-11-26
2021-11-27
2021-11-28
2021-11-29
2021-11-30
2021-12-01
2021-12-02
2021-12-03
2021-12-04
2021-12-05
2021-12-06
2021-12-07
2021-12-08
2021-12-09
2021-12-10
2021-12-11
2021-12-12
2021-12-13
2021-12-14
2021-12-15
2021-12-16
2021-12-17
2021-12-18
2021-12-19
2021-12-20
2021-12-21
2021-12-22
2021-12-23
2021-12-24
2021-12-25
2021-12-26
2021-12-27
2021-12-28
2021-12-29
2021-12-30
2021-12-31
Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Consumption (kWh) with solar
date | mpan_number | ptu_1 | ptu_2 | ptu_3 | ptu_4 | ptu_5 | ptu_6 | ptu_7 | ptu_8 | ptu_9 | ptu_10 | ptu_11 | ptu_12 | ptu_13 | ptu_14 | ptu_15 | ptu_16 | ptu_17 | ptu_18 | ptu_19 | ptu_20 | ptu_21 | ptu_22 | ptu_23 | ptu_24 | ptu_25 | ptu_26 | ptu_27 | ptu_28 | ptu_29 | ptu_30 | ptu_31 | ptu_32 | ptu_33 | ptu_34 | ptu_35 | ptu_36 | ptu_37 | ptu_38 | ptu_39 | ptu_40 | ptu_41 | ptu_42 | ptu_43 | ptu_44 | ptu_45 | ptu_46 | ptu_47 | ptu_48
2021-01-01 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-02 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-03 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-04 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-05 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-06 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-07 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-08 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-09 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-10 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-11 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-12 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-13 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-14 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-15 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-16 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-17 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-18 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-19 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-20 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-21 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-22 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-23 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-24 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-25 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-26 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-27 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-28 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-29 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-30 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-01-31 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-01 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-02 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-03 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-04 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-05 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-06 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-07 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-08 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-09 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-10 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-11 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-12 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-13 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-14 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-15 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-16 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-17 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-18 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-19 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-20 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-21 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-22 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-23 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-24 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-25 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-26 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-27 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-02-28 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-01 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-02 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-03 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-04 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-05 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-06 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-07 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-08 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-09 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-10 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-11 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-12 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-13 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-14 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-15 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-16 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-17 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-18 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-19 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-20 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-21 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-22 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-23 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-24 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-25 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-26 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-27 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-28 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-29 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-30 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-03-31 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-01 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-02 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-03 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-04 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-05 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-06 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-07 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-08 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-09 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-10 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-11 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-12 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-13 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-14 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-15 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-16 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-17 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-18 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-19 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-20 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-21 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-22 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-23 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-24 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-25 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-26 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-27 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-28 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-29 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-04-30 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-01 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-02 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-03 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-04 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-05 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-06 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-07 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-08 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-09 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-10 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-11 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-12 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-13 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-14 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-15 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-16 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-17 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-18 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-19 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-20 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-21 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-22 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-23 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-24 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-25 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-26 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-27 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-28 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-29 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-30 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-31 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-01 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-02 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-03 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-04 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-05 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-06 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-07 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-08 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-09 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-10 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-11 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-12 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-13 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-14 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-15 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-16 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-17 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-18 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-19 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-20 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-21 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-22 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-23 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-24 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-25 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-26 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-27 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-28 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-29 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-06-30 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-01 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-02 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-03 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-04 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-05 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-06 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-07 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-08 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-09 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-10 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-11 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-12 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-13 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-14 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-15 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-16 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-17 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-18 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-19 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-20 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-21 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-22 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-23 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-24 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-25 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-26 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-27 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-28 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-29 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-30 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-07-31 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-01 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-02 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-03 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-04 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-05 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-06 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-07 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-08 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-09 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-10 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-11 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-12 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-13 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-14 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-15 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-16 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-17 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-18 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-19 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-20 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-21 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-22 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-23 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-24 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-25 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-26 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-27 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-28 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-29 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-30 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-31 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-01 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-02 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-03 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-04 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-05 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-06 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-07 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-08 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-09 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-10 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-11 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-12 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-13 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-14 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-15 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-16 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-17 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-18 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-19 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-20 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-21 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-22 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-23 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-24 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-25 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-26 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-27 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-28 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-29 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-09-30 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-01 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-02 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-03 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-04 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-05 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-06 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-07 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-08 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-09 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-10 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-11 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-12 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-13 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-14 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-15 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-16 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-17 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-18 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-19 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-20 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-21 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-22 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-23 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-24 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-25 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-26 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-27 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-28 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-29 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-30 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-31 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-01 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-02 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-03 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-04 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-05 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-06 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-07 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-08 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-09 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-10 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-11 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-12 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-13 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-14 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-15 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-16 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-17 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-18 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-19 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-20 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-21 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-22 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-23 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-24 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-25 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-26 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-27 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-28 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-29 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-11-30 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-01 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-02 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-03 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-04 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-05 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-06 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-07 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-08 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-09 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-10 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-11 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-12 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-13 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-14 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-15 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-16 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-17 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-18 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-19 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-20 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-21 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-22 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-23 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-24 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-25 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-26 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-27 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-28 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-29 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-30 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021-12-31 | S000000000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Solar PV % (hidden)
Date | 0:00 | 0:30 | 1:00 | 1:30 | 2:00 | 2:30 | 3:00 | 3:30 | 4:00 | 4:30 | 5:00 | 5:30 | 6:00 | 6:30 | 7:00 | 7:30 | 8:00 | 8:30 | 9:00 | 9:30 | 10:00 | 10:30 | 11:00 | 11:30 | 12:00 | 12:30 | 13:00 | 13:30 | 14:00 | 14:30 | 15:00 | 15:30 | 16:00 | 16:30 | 17:00 | 17:30 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 20:30 | 21:00 | 21:30 | 22:00 | 22:30 | 23:00 | 23:30
2022-01-01 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002069% | 0.002069% | 0.002676% | 0.002676% | 0.002902% | 0.002902% | 0.003609% | 0.003609% | 0.002855% | 0.002855% | 0.002021% | 0.002021% | 0.00143% | 0.00143% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-02 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004493% | 0.004493% | 0.008734% | 0.008734% | 0.01004% | 0.01004% | 0.01064% | 0.01064% | 0.009824% | 0.009824% | 0.006552% | 0.006552% | 0.002732% | 0.002732% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-03 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00275% | 0.00275% | 0.007671% | 0.007671% | 0.005456% | 0.005456% | 0.00607% | 0.00607% | 0.003775% | 0.003775% | 0.00795% | 0.00795% | 0.00362% | 0.00362% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-04 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004765% | 0.004765% | 0.008288% | 0.008288% | 0.009559% | 0.009559% | 0.006057% | 0.006057% | 0.008858% | 0.008858% | 0.008289% | 0.008289% | 0.003723% | 0.003723% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005386% | 0.005386% | 0.008717% | 0.008717% | 0.01549% | 0.01549% | 0.01406% | 0.01406% | 0.00919% | 0.00919% | 0.007672% | 0.007672% | 0.002794% | 0.002794% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-06 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003652% | 0.003652% | 0.005585% | 0.005585% | 0.01283% | 0.01283% | 0.01356% | 0.01356% | 0.009384% | 0.009384% | 0.007988% | 0.007988% | 0.002465% | 0.002465% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-07 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003066% | 0.003066% | 0.008284% | 0.008284% | 0.006039% | 0.006039% | 0.007104% | 0.007104% | 0.006763% | 0.006763% | 0.007972% | 0.007972% | 0.004135% | 0.004135% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-08 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002245% | 0.002245% | 0.005851% | 0.005851% | 0.005635% | 0.005635% | 0.007565% | 0.007565% | 0.007681% | 0.007681% | 0.004827% | 0.004827% | 0.004587% | 0.004587% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-09 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005292% | 0.005292% | 0.0126% | 0.0126% | 0.01132% | 0.01132% | 0.009492% | 0.009492% | 0.00863% | 0.00863% | 0.00633% | 0.00633% | 0.001597% | 0.001597% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002144% | 0.002144% | 0.004435% | 0.004435% | 0.01003% | 0.01003% | 0.01233% | 0.01233% | 0.01656% | 0.01656% | 0.007472% | 0.007472% | 0.003055% | 0.003055% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-11 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004652% | 0.004652% | 0.009561% | 0.009561% | 0.00821% | 0.00821% | 0.01173% | 0.01173% | 0.01043% | 0.01043% | 0.003248% | 0.003248% | 0.002824% | 0.002824% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-12 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002946% | 0.002946% | 0.006753% | 0.006753% | 0.005303% | 0.005303% | 0.004206% | 0.004206% | 0.002229% | 0.002229% | 0.004846% | 0.004846% | 0.004362% | 0.004362% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-13 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004942% | 0.004942% | 0.006785% | 0.006785% | 0.01245% | 0.01245% | 0.01194% | 0.01194% | 0.005866% | 0.005866% | 0.004706% | 0.004706% | 0.002842% | 0.002842% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002628% | 0.002628% | 0.006487% | 0.006487% | 0.007241% | 0.007241% | 0.00715% | 0.00715% | 0.007513% | 0.007513% | 0.006082% | 0.006082% | 0.003106% | 0.003106% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-15 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003535% | 0.003535% | 0.005298% | 0.005298% | 0.008543% | 0.008543% | 0.0161% | 0.0161% | 0.01435% | 0.01435% | 0.007957% | 0.007957% | 0.007343% | 0.007343% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-16 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005362% | 0.005362% | 0.009683% | 0.009683% | 0.01264% | 0.01264% | 0.01025% | 0.01025% | 0.01253% | 0.01253% | 0.01234% | 0.01234% | 0.006808% | 0.006808% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-17 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.006759% | 0.006759% | 0.0131% | 0.0131% | 0.01406% | 0.01406% | 0.01611% | 0.01611% | 0.01426% | 0.01426% | 0.01138% | 0.01138% | 0.00719% | 0.00719% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-18 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.007422% | 0.007422% | 0.0146% | 0.0146% | 0.01867% | 0.01867% | 0.01535% | 0.01535% | 0.01467% | 0.01467% | 0.0112% | 0.0112% | 0.007428% | 0.007428% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-19 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00767% | 0.00767% | 0.01915% | 0.01915% | 0.02247% | 0.02247% | 0.02327% | 0.02327% | 0.02249% | 0.02249% | 0.01691% | 0.01691% | 0.01052% | 0.01052% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-20 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.006015% | 0.006015% | 0.01178% | 0.01178% | 0.01717% | 0.01717% | 0.01687% | 0.01687% | 0.01686% | 0.01686% | 0.01554% | 0.01554% | 0.00789% | 0.00789% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-21 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005244% | 0.005244% | 0.009874% | 0.009874% | 0.01158% | 0.01158% | 0.01248% | 0.01248% | 0.01501% | 0.01501% | 0.01148% | 0.01148% | 0.007765% | 0.007765% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-22 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00424% | 0.00424% | 0.01079% | 0.01079% | 0.01167% | 0.01167% | 0.01396% | 0.01396% | 0.01118% | 0.01118% | 0.01063% | 0.01063% | 0.004721% | 0.004721% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005097% | 0.005097% | 0.01021% | 0.01021% | 0.01197% | 0.01197% | 0.008035% | 0.008035% | 0.007799% | 0.007799% | 0.007417% | 0.007417% | 0.004498% | 0.004498% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.007067% | 0.007067% | 0.00924% | 0.00924% | 0.01177% | 0.01177% | 0.01394% | 0.01394% | 0.01307% | 0.01307% | 0.008337% | 0.008337% | 0.005571% | 0.005571% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-25 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.007913% | 0.007913% | 0.01028% | 0.01028% | 0.01039% | 0.01039% | 0.008577% | 0.008577% | 0.008206% | 0.008206% | 0.005668% | 0.005668% | 0.003212% | 0.003212% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-26 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002056% | 0.002056% | 0.003154% | 0.003154% | 0.005322% | 0.005322% | 0.01042% | 0.01042% | 0.008415% | 0.008415% | 0.004567% | 0.004567% | 0.002462% | 0.002462% | 0.0003015% | 0.0003015% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-27 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0003906% | 0.0003906% | 0.004839% | 0.004839% | 0.01216% | 0.01216% | 0.01074% | 0.01074% | 0.009798% | 0.009798% | 0.004116% | 0.004116% | 0.002667% | 0.002667% | 0.002121% | 0.002121% | 0.0001776% | 0.0001776% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0005034% | 0.0005034% | 0.00598% | 0.00598% | 0.01164% | 0.01164% | 0.01849% | 0.01849% | 0.01777% | 0.01777% | 0.01426% | 0.01426% | 0.008708% | 0.008708% | 0.01027% | 0.01027% | 0.0007843% | 0.0007843% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-29 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0004507% | 0.0004507% | 0.005967% | 0.005967% | 0.01108% | 0.01108% | 0.01217% | 0.01217% | 0.01278% | 0.01278% | 0.007931% | 0.007931% | 0.009226% | 0.009226% | 0.004869% | 0.004869% | 0.0007199% | 0.0007199% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-30 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0005518% | 0.0005518% | 0.00613% | 0.00613% | 0.009408% | 0.009408% | 0.01319% | 0.01319% | 0.01369% | 0.01369% | 0.01254% | 0.01254% | 0.008204% | 0.008204% | 0.003915% | 0.003915% | 0.001357% | 0.001357% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-01-31 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0003478% | 0.0003478% | 0.002868% | 0.002868% | 0.003514% | 0.003514% | 0.003765% | 0.003765% | 0.005712% | 0.005712% | 0.004432% | 0.004432% | 0.004938% | 0.004938% | 0.004206% | 0.004206% | 0.000549% | 0.000549% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-01 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0006593% | 0.0006593% | 0.007999% | 0.007999% | 0.00887% | 0.00887% | 0.009505% | 0.009505% | 0.007103% | 0.007103% | 0.003664% | 0.003664% | 0.0097% | 0.0097% | 0.00589% | 0.00589% | 0.001313% | 0.001313% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-02 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001289% | 0.001289% | 0.005127% | 0.005127% | 0.007618% | 0.007618% | 0.01182% | 0.01182% | 0.01208% | 0.01208% | 0.01095% | 0.01095% | 0.009818% | 0.009818% | 0.007916% | 0.007916% | 0.001722% | 0.001722% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-03 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001591% | 0.001591% | 0.005156% | 0.005156% | 0.009251% | 0.009251% | 0.008554% | 0.008554% | 0.01048% | 0.01048% | 0.008965% | 0.008965% | 0.005802% | 0.005802% | 0.005483% | 0.005483% | 0.001774% | 0.001774% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-04 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002025% | 0.002025% | 0.004955% | 0.004955% | 0.007109% | 0.007109% | 0.0103% | 0.0103% | 0.009778% | 0.009778% | 0.01001% | 0.01001% | 0.005453% | 0.005453% | 0.005969% | 0.005969% | 0.002546% | 0.002546% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002232% | 0.002232% | 0.004374% | 0.004374% | 0.006587% | 0.006587% | 0.009% | 0.009% | 0.01083% | 0.01083% | 0.00923% | 0.00923% | 0.005911% | 0.005911% | 0.005521% | 0.005521% | 0.003028% | 0.003028% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-06 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00253% | 0.00253% | 0.01005% | 0.01005% | 0.01811% | 0.01811% | 0.01832% | 0.01832% | 0.01354% | 0.01354% | 0.017% | 0.017% | 0.01503% | 0.01503% | 0.009346% | 0.009346% | 0.004028% | 0.004028% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-07 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003863% | 0.003863% | 0.009356% | 0.009356% | 0.01353% | 0.01353% | 0.01515% | 0.01515% | 0.01513% | 0.01513% | 0.01702% | 0.01702% | 0.01489% | 0.01489% | 0.006251% | 0.006251% | 0.002535% | 0.002535% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-08 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002453% | 0.002453% | 0.009015% | 0.009015% | 0.01186% | 0.01186% | 0.01652% | 0.01652% | 0.01519% | 0.01519% | 0.01565% | 0.01565% | 0.01175% | 0.01175% | 0.008372% | 0.008372% | 0.004071% | 0.004071% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-09 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001048% | 0.001048% | 0.002821% | 0.002821% | 0.007005% | 0.007005% | 0.008555% | 0.008555% | 0.01176% | 0.01176% | 0.01228% | 0.01228% | 0.01049% | 0.01049% | 0.006327% | 0.006327% | 0.003561% | 0.003561% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003125% | 0.003125% | 0.004546% | 0.004546% | 0.007583% | 0.007583% | 0.00787% | 0.00787% | 0.00726% | 0.00726% | 0.004901% | 0.004901% | 0.00829% | 0.00829% | 0.003537% | 0.003537% | 0.001406% | 0.001406% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-11 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005113% | 0.005113% | 0.01096% | 0.01096% | 0.01567% | 0.01567% | 0.01787% | 0.01787% | 0.01283% | 0.01283% | 0.01107% | 0.01107% | 0.01218% | 0.01218% | 0.00829% | 0.00829% | 0.004594% | 0.004594% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-12 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004979% | 0.004979% | 0.009337% | 0.009337% | 0.01185% | 0.01185% | 0.01332% | 0.01332% | 0.01338% | 0.01338% | 0.009896% | 0.009896% | 0.01034% | 0.01034% | 0.009288% | 0.009288% | 0.00351% | 0.00351% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-13 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00315% | 0.00315% | 0.00522% | 0.00522% | 0.01204% | 0.01204% | 0.009872% | 0.009872% | 0.01037% | 0.01037% | 0.01427% | 0.01427% | 0.008989% | 0.008989% | 0.007497% | 0.007497% | 0.004169% | 0.004169% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.006581% | 0.006581% | 0.01079% | 0.01079% | 0.01377% | 0.01377% | 0.01386% | 0.01386% | 0.00882% | 0.00882% | 0.01004% | 0.01004% | 0.006371% | 0.006371% | 0.009252% | 0.009252% | 0.002062% | 0.002062% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-15 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002866% | 0.002866% | 0.00677% | 0.00677% | 0.01095% | 0.01095% | 0.0109% | 0.0109% | 0.009682% | 0.009682% | 0.009887% | 0.009887% | 0.01029% | 0.01029% | 0.01009% | 0.01009% | 0.005064% | 0.005064% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-16 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005261% | 0.005261% | 0.008802% | 0.008802% | 0.01668% | 0.01668% | 0.01801% | 0.01801% | 0.01841% | 0.01841% | 0.01666% | 0.01666% | 0.01613% | 0.01613% | 0.008837% | 0.008837% | 0.002913% | 0.002913% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-17 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.006186% | 0.006186% | 0.01222% | 0.01222% | 0.01649% | 0.01649% | 0.02075% | 0.02075% | 0.02227% | 0.02227% | 0.01806% | 0.01806% | 0.02123% | 0.02123% | 0.0149% | 0.0149% | 0.008062% | 0.008062% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-18 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005447% | 0.005447% | 0.01185% | 0.01185% | 0.01872% | 0.01872% | 0.02309% | 0.02309% | 0.02049% | 0.02049% | 0.01894% | 0.01894% | 0.01403% | 0.01403% | 0.01177% | 0.01177% | 0.006776% | 0.006776% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-19 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004945% | 0.004945% | 0.01017% | 0.01017% | 0.01027% | 0.01027% | 0.01124% | 0.01124% | 0.008319% | 0.008319% | 0.009394% | 0.009394% | 0.008079% | 0.008079% | 0.004807% | 0.004807% | 0.002172% | 0.002172% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-20 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003958% | 0.003958% | 0.006529% | 0.006529% | 0.006878% | 0.006878% | 0.01329% | 0.01329% | 0.009789% | 0.009789% | 0.005652% | 0.005652% | 0.005301% | 0.005301% | 0.00335% | 0.00335% | 0.002164% | 0.002164% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-21 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004045% | 0.004045% | 0.009552% | 0.009552% | 0.01099% | 0.01099% | 0.009231% | 0.009231% | 0.003502% | 0.003502% | 0.009565% | 0.009565% | 0.007092% | 0.007092% | 0.005825% | 0.005825% | 0.00307% | 0.00307% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-22 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00415% | 0.00415% | 0.005418% | 0.005418% | 0.007466% | 0.007466% | 0.01098% | 0.01098% | 0.009495% | 0.009495% | 0.0113% | 0.0113% | 0.009739% | 0.009739% | 0.007621% | 0.007621% | 0.005468% | 0.005468% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005798% | 0.005798% | 0.01037% | 0.01037% | 0.009335% | 0.009335% | 0.01174% | 0.01174% | 0.006704% | 0.006704% | 0.006563% | 0.006563% | 0.01422% | 0.01422% | 0.009033% | 0.009033% | 0.004399% | 0.004399% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.007972% | 0.007972% | 0.01651% | 0.01651% | 0.02082% | 0.02082% | 0.02237% | 0.02237% | 0.01695% | 0.01695% | 0.01934% | 0.01934% | 0.01312% | 0.01312% | 0.01343% | 0.01343% | 0.008138% | 0.008138% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-25 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.007631% | 0.007631% | 0.01231% | 0.01231% | 0.01148% | 0.01148% | 0.01509% | 0.01509% | 0.01306% | 0.01306% | 0.01616% | 0.01616% | 0.01227% | 0.01227% | 0.01016% | 0.01016% | 0.005854% | 0.005854% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-26 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004782% | 0.004782% | 0.008252% | 0.008252% | 0.008125% | 0.008125% | 0.01464% | 0.01464% | 0.01428% | 0.01428% | 0.009419% | 0.009419% | 0.01022% | 0.01022% | 0.005421% | 0.005421% | 0.00542% | 0.00542% | 0.0003433% | 0.0003433% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-27 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.008418% | 0.008418% | 0.01075% | 0.01075% | 0.0104% | 0.0104% | 0.01148% | 0.01148% | 0.009997% | 0.009997% | 0.01368% | 0.01368% | 0.01274% | 0.01274% | 0.01076% | 0.01076% | 0.007277% | 0.007277% | 0.0008039% | 0.0008039% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-02-28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0002544% | 0.0002544% | 0.005172% | 0.005172% | 0.01002% | 0.01002% | 0.01346% | 0.01346% | 0.0107% | 0.0107% | 0.007979% | 0.007979% | 0.01011% | 0.01011% | 0.005484% | 0.005484% | 0.007532% | 0.007532% | 0.00324% | 0.00324% | 0.0005037% | 0.0005037% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-01 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0004503% | 0.0004503% | 0.00648% | 0.00648% | 0.009208% | 0.009208% | 0.01353% | 0.01353% | 0.01166% | 0.01166% | 0.01262% | 0.01262% | 0.01818% | 0.01818% | 0.01195% | 0.01195% | 0.01034% | 0.01034% | 0.005837% | 0.005837% | 0.0009552% | 0.0009552% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-02 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001225% | 0.001225% | 0.00328% | 0.00328% | 0.007174% | 0.007174% | 0.009145% | 0.009145% | 0.009853% | 0.009853% | 0.009117% | 0.009117% | 0.01651% | 0.01651% | 0.01448% | 0.01448% | 0.01059% | 0.01059% | 0.008765% | 0.008765% | 0.001818% | 0.001818% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-03 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001126% | 0.001126% | 0.007733% | 0.007733% | 0.009776% | 0.009776% | 0.01319% | 0.01319% | 0.01605% | 0.01605% | 0.006599% | 0.006599% | 0.01438% | 0.01438% | 0.01473% | 0.01473% | 0.01003% | 0.01003% | 0.005791% | 0.005791% | 0.001102% | 0.001102% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-04 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001424% | 0.001424% | 0.01006% | 0.01006% | 0.01538% | 0.01538% | 0.0174% | 0.0174% | 0.01917% | 0.01917% | 0.01126% | 0.01126% | 0.01252% | 0.01252% | 0.008933% | 0.008933% | 0.01036% | 0.01036% | 0.004303% | 0.004303% | 0.0006798% | 0.0006798% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001122% | 0.001122% | 0.006006% | 0.006006% | 0.01091% | 0.01091% | 0.01506% | 0.01506% | 0.01327% | 0.01327% | 0.01529% | 0.01529% | 0.0136% | 0.0136% | 0.01099% | 0.01099% | 0.0065% | 0.0065% | 0.003311% | 0.003311% | 0.00109% | 0.00109% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-06 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001848% | 0.001848% | 0.008965% | 0.008965% | 0.01629% | 0.01629% | 0.01864% | 0.01864% | 0.02286% | 0.02286% | 0.01923% | 0.01923% | 0.01856% | 0.01856% | 0.01603% | 0.01603% | 0.01334% | 0.01334% | 0.008466% | 0.008466% | 0.001824% | 0.001824% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-07 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001547% | 0.001547% | 0.007143% | 0.007143% | 0.01278% | 0.01278% | 0.01561% | 0.01561% | 0.02298% | 0.02298% | 0.02029% | 0.02029% | 0.02087% | 0.02087% | 0.01763% | 0.01763% | 0.01331% | 0.01331% | 0.008975% | 0.008975% | 0.002751% | 0.002751% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-08 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001484% | 0.001484% | 0.009001% | 0.009001% | 0.01262% | 0.01262% | 0.01633% | 0.01633% | 0.01497% | 0.01497% | 0.01354% | 0.01354% | 0.01169% | 0.01169% | 0.01081% | 0.01081% | 0.009534% | 0.009534% | 0.007279% | 0.007279% | 0.002369% | 0.002369% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-09 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002196% | 0.002196% | 0.008898% | 0.008898% | 0.01207% | 0.01207% | 0.008047% | 0.008047% | 0.01092% | 0.01092% | 0.01238% | 0.01238% | 0.01634% | 0.01634% | 0.009703% | 0.009703% | 0.009258% | 0.009258% | 0.004271% | 0.004271% | 0.001527% | 0.001527% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001412% | 0.001412% | 0.004047% | 0.004047% | 0.00706% | 0.00706% | 0.01049% | 0.01049% | 0.01139% | 0.01139% | 0.01319% | 0.01319% | 0.01065% | 0.01065% | 0.009907% | 0.009907% | 0.007752% | 0.007752% | 0.005565% | 0.005565% | 0.002083% | 0.002083% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-11 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002322% | 0.002322% | 0.007816% | 0.007816% | 0.01351% | 0.01351% | 0.02151% | 0.02151% | 0.02476% | 0.02476% | 0.02284% | 0.02284% | 0.02241% | 0.02241% | 0.01456% | 0.01456% | 0.01572% | 0.01572% | 0.01003% | 0.01003% | 0.002478% | 0.002478% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-12 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002541% | 0.002541% | 0.007304% | 0.007304% | 0.01201% | 0.01201% | 0.01127% | 0.01127% | 0.02043% | 0.02043% | 0.02186% | 0.02186% | 0.0207% | 0.0207% | 0.0138% | 0.0138% | 0.01113% | 0.01113% | 0.005602% | 0.005602% | 0.002435% | 0.002435% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-13 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003322% | 0.003322% | 0.009953% | 0.009953% | 0.01021% | 0.01021% | 0.01721% | 0.01721% | 0.01907% | 0.01907% | 0.0198% | 0.0198% | 0.02292% | 0.02292% | 0.02093% | 0.02093% | 0.01729% | 0.01729% | 0.01138% | 0.01138% | 0.003529% | 0.003529% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002502% | 0.002502% | 0.007744% | 0.007744% | 0.01379% | 0.01379% | 0.02008% | 0.02008% | 0.01672% | 0.01672% | 0.01644% | 0.01644% | 0.02071% | 0.02071% | 0.01834% | 0.01834% | 0.01373% | 0.01373% | 0.008655% | 0.008655% | 0.002663% | 0.002663% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-15 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001758% | 0.001758% | 0.00487% | 0.00487% | 0.007509% | 0.007509% | 0.009843% | 0.009843% | 0.01291% | 0.01291% | 0.01285% | 0.01285% | 0.01002% | 0.01002% | 0.009682% | 0.009682% | 0.009114% | 0.009114% | 0.005998% | 0.005998% | 0.00305% | 0.00305% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-16 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004066% | 0.004066% | 0.01028% | 0.01028% | 0.01674% | 0.01674% | 0.01954% | 0.01954% | 0.02372% | 0.02372% | 0.01645% | 0.01645% | 0.01991% | 0.01991% | 0.02016% | 0.02016% | 0.0154% | 0.0154% | 0.01127% | 0.01127% | 0.003496% | 0.003496% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-17 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003408% | 0.003408% | 0.009799% | 0.009799% | 0.01474% | 0.01474% | 0.01923% | 0.01923% | 0.01942% | 0.01942% | 0.01835% | 0.01835% | 0.01757% | 0.01757% | 0.01512% | 0.01512% | 0.01134% | 0.01134% | 0.006977% | 0.006977% | 0.002416% | 0.002416% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-18 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002597% | 0.002597% | 0.005262% | 0.005262% | 0.006455% | 0.006455% | 0.009723% | 0.009723% | 0.0137% | 0.0137% | 0.01136% | 0.01136% | 0.01308% | 0.01308% | 0.01003% | 0.01003% | 0.01003% | 0.01003% | 0.005703% | 0.005703% | 0.002841% | 0.002841% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-19 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001811% | 0.001811% | 0.003654% | 0.003654% | 0.004349% | 0.004349% | 0.004645% | 0.004645% | 0.00405% | 0.00405% | 0.004459% | 0.004459% | 0.00911% | 0.00911% | 0.01064% | 0.01064% | 0.007731% | 0.007731% | 0.006289% | 0.006289% | 0.002973% | 0.002973% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-20 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00272% | 0.00272% | 0.005206% | 0.005206% | 0.01073% | 0.01073% | 0.01024% | 0.01024% | 0.009742% | 0.009742% | 0.014% | 0.014% | 0.01389% | 0.01389% | 0.01342% | 0.01342% | 0.01147% | 0.01147% | 0.008133% | 0.008133% | 0.004548% | 0.004548% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-21 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005743% | 0.005743% | 0.0111% | 0.0111% | 0.01666% | 0.01666% | 0.02365% | 0.02365% | 0.0251% | 0.0251% | 0.02192% | 0.02192% | 0.01952% | 0.01952% | 0.01968% | 0.01968% | 0.01257% | 0.01257% | 0.009409% | 0.009409% | 0.003901% | 0.003901% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-22 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004339% | 0.004339% | 0.01203% | 0.01203% | 0.02117% | 0.02117% | 0.02253% | 0.02253% | 0.02218% | 0.02218% | 0.01927% | 0.01927% | 0.01962% | 0.01962% | 0.02038% | 0.02038% | 0.01548% | 0.01548% | 0.009826% | 0.009826% | 0.003615% | 0.003615% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004245% | 0.004245% | 0.008865% | 0.008865% | 0.01742% | 0.01742% | 0.02196% | 0.02196% | 0.02377% | 0.02377% | 0.02341% | 0.02341% | 0.01918% | 0.01918% | 0.01842% | 0.01842% | 0.01341% | 0.01341% | 0.00966% | 0.00966% | 0.004526% | 0.004526% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003854% | 0.003854% | 0.006944% | 0.006944% | 0.01146% | 0.01146% | 0.01594% | 0.01594% | 0.01512% | 0.01512% | 0.01158% | 0.01158% | 0.0137% | 0.0137% | 0.0151% | 0.0151% | 0.01656% | 0.01656% | 0.009815% | 0.009815% | 0.003559% | 0.003559% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-25 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.006211% | 0.006211% | 0.01423% | 0.01423% | 0.02217% | 0.02217% | 0.02361% | 0.02361% | 0.02678% | 0.02678% | 0.02302% | 0.02302% | 0.02738% | 0.02738% | 0.0222% | 0.0222% | 0.01965% | 0.01965% | 0.01487% | 0.01487% | 0.007143% | 0.007143% | 0.0002221% | 0.0002221% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-26 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 6.668e-05% | 6.668e-05% | 0.002857% | 0.002857% | 0.008115% | 0.008115% | 0.01303% | 0.01303% | 0.01946% | 0.01946% | 0.02511% | 0.02511% | 0.02626% | 0.02626% | 0.01884% | 0.01884% | 0.01681% | 0.01681% | 0.0168% | 0.0168% | 0.0113% | 0.0113% | 0.006669% | 0.006669% | 0.002317% | 0.002317% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-27 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0001481% | 0.0001481% | 0.003263% | 0.003263% | 0.007888% | 0.007888% | 0.01302% | 0.01302% | 0.02156% | 0.02156% | 0.02322% | 0.02322% | 0.0287% | 0.0287% | 0.02796% | 0.02796% | 0.02173% | 0.02173% | 0.02173% | 0.02173% | 0.0176% | 0.0176% | 0.009746% | 0.009746% | 0.002103% | 0.002103% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0001481% | 0.0001481% | 0.002136% | 0.002136% | 0.006123% | 0.006123% | 0.01049% | 0.01049% | 0.01659% | 0.01659% | 0.02615% | 0.02615% | 0.01928% | 0.01928% | 0.01549% | 0.01549% | 0.01279% | 0.01279% | 0.014% | 0.014% | 0.01451% | 0.01451% | 0.006671% | 0.006671% | 0.001374% | 0.001374% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-29 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0005058% | 0.0005058% | 0.006218% | 0.006218% | 0.01221% | 0.01221% | 0.01515% | 0.01515% | 0.009394% | 0.009394% | 0.01537% | 0.01537% | 0.01275% | 0.01275% | 0.01417% | 0.01417% | 0.01196% | 0.01196% | 0.008937% | 0.008937% | 0.004072% | 0.004072% | 0.003174% | 0.003174% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-30 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0005535% | 0.0005535% | 0.00614% | 0.00614% | 0.008785% | 0.008785% | 0.01678% | 0.01678% | 0.01935% | 0.01935% | 0.01992% | 0.01992% | 0.01618% | 0.01618% | 0.01499% | 0.01499% | 0.01264% | 0.01264% | 0.01159% | 0.01159% | 0.006697% | 0.006697% | 0.003066% | 0.003066% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-03-31 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00053% | 0.00053% | 0.005337% | 0.005337% | 0.01308% | 0.01308% | 0.01597% | 0.01597% | 0.01696% | 0.01696% | 0.01712% | 0.01712% | 0.01774% | 0.01774% | 0.016% | 0.016% | 0.01517% | 0.01517% | 0.01039% | 0.01039% | 0.01146% | 0.01146% | 0.005893% | 0.005893% | 0.0001531% | 0.0001531% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-01 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0009392% | 0.0009392% | 0.006954% | 0.006954% | 0.01473% | 0.01473% | 0.02175% | 0.02175% | 0.01843% | 0.01843% | 0.01543% | 0.01543% | 0.01245% | 0.01245% | 0.01415% | 0.01415% | 0.0111% | 0.0111% | 0.00995% | 0.00995% | 0.006703% | 0.006703% | 0.003738% | 0.003738% | 0.0002576% | 0.0002576% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-02 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0007725% | 0.0007725% | 0.004566% | 0.004566% | 0.01147% | 0.01147% | 0.0184% | 0.0184% | 0.01726% | 0.01726% | 0.01858% | 0.01858% | 0.02321% | 0.02321% | 0.01926% | 0.01926% | 0.01541% | 0.01541% | 0.01262% | 0.01262% | 0.006726% | 0.006726% | 0.002711% | 0.002711% | 0.0002704% | 0.0002704% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-03 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0008574% | 0.0008574% | 0.004773% | 0.004773% | 0.01163% | 0.01163% | 0.0136% | 0.0136% | 0.01599% | 0.01599% | 0.01712% | 0.01712% | 0.01944% | 0.01944% | 0.01808% | 0.01808% | 0.01514% | 0.01514% | 0.01415% | 0.01415% | 0.009213% | 0.009213% | 0.003403% | 0.003403% | 0.0003144% | 0.0003144% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-04 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001079% | 0.001079% | 0.004902% | 0.004902% | 0.009093% | 0.009093% | 0.01472% | 0.01472% | 0.01367% | 0.01367% | 0.01565% | 0.01565% | 0.01506% | 0.01506% | 0.01271% | 0.01271% | 0.01087% | 0.01087% | 0.01256% | 0.01256% | 0.007445% | 0.007445% | 0.004924% | 0.004924% | 0.0004284% | 0.0004284% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001422% | 0.001422% | 0.008786% | 0.008786% | 0.01725% | 0.01725% | 0.02313% | 0.02313% | 0.026% | 0.026% | 0.02993% | 0.02993% | 0.0276% | 0.0276% | 0.03183% | 0.03183% | 0.02583% | 0.02583% | 0.02309% | 0.02309% | 0.01469% | 0.01469% | 0.00639% | 0.00639% | 0.0005839% | 0.0005839% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-06 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001334% | 0.001334% | 0.00583% | 0.00583% | 0.01039% | 0.01039% | 0.01582% | 0.01582% | 0.02277% | 0.02277% | 0.02959% | 0.02959% | 0.03225% | 0.03225% | 0.02625% | 0.02625% | 0.0245% | 0.0245% | 0.01824% | 0.01824% | 0.01293% | 0.01293% | 0.005771% | 0.005771% | 0.0006299% | 0.0006299% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-07 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001847% | 0.001847% | 0.007884% | 0.007884% | 0.01463% | 0.01463% | 0.0199% | 0.0199% | 0.02563% | 0.02563% | 0.02609% | 0.02609% | 0.02579% | 0.02579% | 0.02507% | 0.02507% | 0.02182% | 0.02182% | 0.02016% | 0.02016% | 0.0118% | 0.0118% | 0.005177% | 0.005177% | 0.0005934% | 0.0005934% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-08 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002031% | 0.002031% | 0.00727% | 0.00727% | 0.01265% | 0.01265% | 0.01775% | 0.01775% | 0.02259% | 0.02259% | 0.02456% | 0.02456% | 0.01822% | 0.01822% | 0.0187% | 0.0187% | 0.01689% | 0.01689% | 0.01535% | 0.01535% | 0.01025% | 0.01025% | 0.004842% | 0.004842% | 0.0006896% | 0.0006896% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-09 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001852% | 0.001852% | 0.00662% | 0.00662% | 0.01199% | 0.01199% | 0.02005% | 0.02005% | 0.0264% | 0.0264% | 0.02797% | 0.02797% | 0.02792% | 0.02792% | 0.02753% | 0.02753% | 0.02024% | 0.02024% | 0.01702% | 0.01702% | 0.01134% | 0.01134% | 0.005701% | 0.005701% | 0.0006619% | 0.0006619% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002122% | 0.002122% | 0.009044% | 0.009044% | 0.01469% | 0.01469% | 0.02289% | 0.02289% | 0.02315% | 0.02315% | 0.02569% | 0.02569% | 0.02528% | 0.02528% | 0.02253% | 0.02253% | 0.02007% | 0.02007% | 0.01598% | 0.01598% | 0.009942% | 0.009942% | 0.005527% | 0.005527% | 0.0008977% | 0.0008977% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-11 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00186% | 0.00186% | 0.006167% | 0.006167% | 0.01251% | 0.01251% | 0.01588% | 0.01588% | 0.02189% | 0.02189% | 0.02834% | 0.02834% | 0.02484% | 0.02484% | 0.02088% | 0.02088% | 0.01295% | 0.01295% | 0.01202% | 0.01202% | 0.009866% | 0.009866% | 0.005643% | 0.005643% | 0.0009337% | 0.0009337% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-12 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002437% | 0.002437% | 0.006329% | 0.006329% | 0.01312% | 0.01312% | 0.01968% | 0.01968% | 0.0236% | 0.0236% | 0.025% | 0.025% | 0.028% | 0.028% | 0.02199% | 0.02199% | 0.02135% | 0.02135% | 0.02074% | 0.02074% | 0.01335% | 0.01335% | 0.005736% | 0.005736% | 0.0008406% | 0.0008406% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-13 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002119% | 0.002119% | 0.006907% | 0.006907% | 0.01041% | 0.01041% | 0.01413% | 0.01413% | 0.01854% | 0.01854% | 0.01696% | 0.01696% | 0.02063% | 0.02063% | 0.02229% | 0.02229% | 0.01751% | 0.01751% | 0.01502% | 0.01502% | 0.01012% | 0.01012% | 0.005241% | 0.005241% | 0.001098% | 0.001098% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002778% | 0.002778% | 0.009708% | 0.009708% | 0.01534% | 0.01534% | 0.02331% | 0.02331% | 0.02693% | 0.02693% | 0.03175% | 0.03175% | 0.03271% | 0.03271% | 0.02798% | 0.02798% | 0.02129% | 0.02129% | 0.01931% | 0.01931% | 0.01329% | 0.01329% | 0.006423% | 0.006423% | 0.0009066% | 0.0009066% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-15 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002293% | 0.002293% | 0.008174% | 0.008174% | 0.01302% | 0.01302% | 0.01786% | 0.01786% | 0.02123% | 0.02123% | 0.02536% | 0.02536% | 0.02799% | 0.02799% | 0.02691% | 0.02691% | 0.02058% | 0.02058% | 0.0168% | 0.0168% | 0.01238% | 0.01238% | 0.006577% | 0.006577% | 0.001395% | 0.001395% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-16 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002898% | 0.002898% | 0.007878% | 0.007878% | 0.01588% | 0.01588% | 0.0238% | 0.0238% | 0.02203% | 0.02203% | 0.02136% | 0.02136% | 0.01948% | 0.01948% | 0.01577% | 0.01577% | 0.01184% | 0.01184% | 0.01207% | 0.01207% | 0.008227% | 0.008227% | 0.005514% | 0.005514% | 0.001448% | 0.001448% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-17 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0032% | 0.0032% | 0.009107% | 0.009107% | 0.01479% | 0.01479% | 0.02053% | 0.02053% | 0.02411% | 0.02411% | 0.02418% | 0.02418% | 0.02347% | 0.02347% | 0.02067% | 0.02067% | 0.0197% | 0.0197% | 0.01498% | 0.01498% | 0.01009% | 0.01009% | 0.005144% | 0.005144% | 0.001194% | 0.001194% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-18 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003603% | 0.003603% | 0.009305% | 0.009305% | 0.01684% | 0.01684% | 0.02229% | 0.02229% | 0.01993% | 0.01993% | 0.02466% | 0.02466% | 0.02557% | 0.02557% | 0.02529% | 0.02529% | 0.02257% | 0.02257% | 0.01865% | 0.01865% | 0.01282% | 0.01282% | 0.006415% | 0.006415% | 0.001495% | 0.001495% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-19 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003393% | 0.003393% | 0.01016% | 0.01016% | 0.01748% | 0.01748% | 0.02289% | 0.02289% | 0.02846% | 0.02846% | 0.03463% | 0.03463% | 0.03361% | 0.03361% | 0.03225% | 0.03225% | 0.02843% | 0.02843% | 0.02244% | 0.02244% | 0.01768% | 0.01768% | 0.008498% | 0.008498% | 0.001569% | 0.001569% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-20 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003855% | 0.003855% | 0.01214% | 0.01214% | 0.02117% | 0.02117% | 0.02895% | 0.02895% | 0.03278% | 0.03278% | 0.03613% | 0.03613% | 0.03709% | 0.03709% | 0.03452% | 0.03452% | 0.02819% | 0.02819% | 0.02428% | 0.02428% | 0.01656% | 0.01656% | 0.008552% | 0.008552% | 0.0017% | 0.0017% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-21 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003167% | 0.003167% | 0.008939% | 0.008939% | 0.0156% | 0.0156% | 0.02281% | 0.02281% | 0.02829% | 0.02829% | 0.03474% | 0.03474% | 0.0311% | 0.0311% | 0.03031% | 0.03031% | 0.0244% | 0.0244% | 0.01788% | 0.01788% | 0.01027% | 0.01027% | 0.006535% | 0.006535% | 0.001482% | 0.001482% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-22 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003752% | 0.003752% | 0.009202% | 0.009202% | 0.01515% | 0.01515% | 0.02017% | 0.02017% | 0.02374% | 0.02374% | 0.02707% | 0.02707% | 0.02841% | 0.02841% | 0.02727% | 0.02727% | 0.02425% | 0.02425% | 0.01331% | 0.01331% | 0.01226% | 0.01226% | 0.005592% | 0.005592% | 0.001381% | 0.001381% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0001346% | 0.0001346% | 0.003778% | 0.003778% | 0.009707% | 0.009707% | 0.01378% | 0.01378% | 0.01727% | 0.01727% | 0.01974% | 0.01974% | 0.0212% | 0.0212% | 0.02467% | 0.02467% | 0.02575% | 0.02575% | 0.0223% | 0.0223% | 0.02018% | 0.02018% | 0.01482% | 0.01482% | 0.007465% | 0.007465% | 0.001989% | 0.001989% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0002692% | 0.0002692% | 0.003639% | 0.003639% | 0.008249% | 0.008249% | 0.01586% | 0.01586% | 0.01669% | 0.01669% | 0.02051% | 0.02051% | 0.02713% | 0.02713% | 0.02254% | 0.02254% | 0.02164% | 0.02164% | 0.01514% | 0.01514% | 0.01393% | 0.01393% | 0.008467% | 0.008467% | 0.004188% | 0.004188% | 0.001543% | 0.001543% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-25 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0001984% | 0.0001984% | 0.003105% | 0.003105% | 0.007213% | 0.007213% | 0.01209% | 0.01209% | 0.01497% | 0.01497% | 0.02107% | 0.02107% | 0.0221% | 0.0221% | 0.01419% | 0.01419% | 0.01726% | 0.01726% | 0.02137% | 0.02137% | 0.01928% | 0.01928% | 0.01387% | 0.01387% | 0.005621% | 0.005621% | 0.001618% | 0.001618% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-26 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0004038% | 0.0004038% | 0.004222% | 0.004222% | 0.01034% | 0.01034% | 0.01408% | 0.01408% | 0.01951% | 0.01951% | 0.02102% | 0.02102% | 0.02213% | 0.02213% | 0.02169% | 0.02169% | 0.01753% | 0.01753% | 0.01769% | 0.01769% | 0.01561% | 0.01561% | 0.01287% | 0.01287% | 0.007044% | 0.007044% | 0.001975% | 0.001975% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-27 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0004604% | 0.0004604% | 0.003896% | 0.003896% | 0.009817% | 0.009817% | 0.01668% | 0.01668% | 0.01999% | 0.01999% | 0.01692% | 0.01692% | 0.02276% | 0.02276% | 0.0113% | 0.0113% | 0.01472% | 0.01472% | 0.01351% | 0.01351% | 0.01103% | 0.01103% | 0.01134% | 0.01134% | 0.005453% | 0.005453% | 0.001357% | 0.001357% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0004818% | 0.0004818% | 0.00406% | 0.00406% | 0.008082% | 0.008082% | 0.009267% | 0.009267% | 0.01512% | 0.01512% | 0.01687% | 0.01687% | 0.01959% | 0.01959% | 0.009617% | 0.009617% | 0.01545% | 0.01545% | 0.01445% | 0.01445% | 0.0117% | 0.0117% | 0.007454% | 0.007454% | 0.004123% | 0.004123% | 0.00186% | 0.00186% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-29 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00051% | 0.00051% | 0.003068% | 0.003068% | 0.007715% | 0.007715% | 0.01307% | 0.01307% | 0.0169% | 0.0169% | 0.01124% | 0.01124% | 0.01204% | 0.01204% | 0.01322% | 0.01322% | 0.01138% | 0.01138% | 0.01224% | 0.01224% | 0.01415% | 0.01415% | 0.01058% | 0.01058% | 0.006748% | 0.006748% | 0.001898% | 0.001898% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-04-30 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.000595% | 0.000595% | 0.004247% | 0.004247% | 0.01004% | 0.01004% | 0.01475% | 0.01475% | 0.01659% | 0.01659% | 0.02029% | 0.02029% | 0.02136% | 0.02136% | 0.02043% | 0.02043% | 0.01497% | 0.01497% | 0.009905% | 0.009905% | 0.01076% | 0.01076% | 0.008748% | 0.008748% | 0.006793% | 0.006793% | 0.002096% | 0.002096% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-01 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0008146% | 0.0008146% | 0.00412% | 0.00412% | 0.01069% | 0.01069% | 0.01799% | 0.01799% | 0.02052% | 0.02052% | 0.02123% | 0.02123% | 0.02496% | 0.02496% | 0.02449% | 0.02449% | 0.03011% | 0.03011% | 0.02385% | 0.02385% | 0.01587% | 0.01587% | 0.01026% | 0.01026% | 0.006077% | 0.006077% | 0.002249% | 0.002249% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-02 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0006942% | 0.0006942% | 0.00332% | 0.00332% | 0.006258% | 0.006258% | 0.01134% | 0.01134% | 0.01558% | 0.01558% | 0.02083% | 0.02083% | 0.01998% | 0.01998% | 0.01944% | 0.01944% | 0.01976% | 0.01976% | 0.01122% | 0.01122% | 0.01107% | 0.01107% | 0.005994% | 0.005994% | 0.004463% | 0.004463% | 0.001921% | 0.001921% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-03 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.000843% | 0.000843% | 0.003789% | 0.003789% | 0.005204% | 0.005204% | 0.01% | 0.01% | 0.01523% | 0.01523% | 0.01869% | 0.01869% | 0.0203% | 0.0203% | 0.01627% | 0.01627% | 0.01458% | 0.01458% | 0.01837% | 0.01837% | 0.0167% | 0.0167% | 0.01056% | 0.01056% | 0.006671% | 0.006671% | 0.002215% | 0.002215% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-04 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.000765% | 0.000765% | 0.004051% | 0.004051% | 0.006942% | 0.006942% | 0.01812% | 0.01812% | 0.02368% | 0.02368% | 0.02623% | 0.02623% | 0.02988% | 0.02988% | 0.02866% | 0.02866% | 0.02756% | 0.02756% | 0.01814% | 0.01814% | 0.01665% | 0.01665% | 0.01252% | 0.01252% | 0.007115% | 0.007115% | 0.002067% | 0.002067% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00102% | 0.00102% | 0.005398% | 0.005398% | 0.01081% | 0.01081% | 0.0189% | 0.0189% | 0.02316% | 0.02316% | 0.02469% | 0.02469% | 0.03181% | 0.03181% | 0.03406% | 0.03406% | 0.03376% | 0.03376% | 0.02953% | 0.02953% | 0.02238% | 0.02238% | 0.01394% | 0.01394% | 0.007772% | 0.007772% | 0.002273% | 0.002273% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-06 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001147% | 0.001147% | 0.005139% | 0.005139% | 0.01277% | 0.01277% | 0.01991% | 0.01991% | 0.02538% | 0.02538% | 0.02839% | 0.02839% | 0.02836% | 0.02836% | 0.03133% | 0.03133% | 0.02756% | 0.02756% | 0.02838% | 0.02838% | 0.02343% | 0.02343% | 0.01567% | 0.01567% | 0.007065% | 0.007065% | 0.002169% | 0.002169% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-07 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001169% | 0.001169% | 0.004786% | 0.004786% | 0.01107% | 0.01107% | 0.01522% | 0.01522% | 0.02341% | 0.02341% | 0.02798% | 0.02798% | 0.02825% | 0.02825% | 0.02951% | 0.02951% | 0.02661% | 0.02661% | 0.02493% | 0.02493% | 0.02082% | 0.02082% | 0.01577% | 0.01577% | 0.00924% | 0.00924% | 0.002592% | 0.002592% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-08 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00114% | 0.00114% | 0.004519% | 0.004519% | 0.009449% | 0.009449% | 0.01635% | 0.01635% | 0.02039% | 0.02039% | 0.02231% | 0.02231% | 0.02739% | 0.02739% | 0.02886% | 0.02886% | 0.02258% | 0.02258% | 0.01912% | 0.01912% | 0.01678% | 0.01678% | 0.0109% | 0.0109% | 0.008012% | 0.008012% | 0.002582% | 0.002582% | 1.424e-05% | 1.424e-05% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-09 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001048% | 0.001048% | 0.005327% | 0.005327% | 0.01014% | 0.01014% | 0.01706% | 0.01706% | 0.0204% | 0.0204% | 0.02616% | 0.02616% | 0.02939% | 0.02939% | 0.029% | 0.029% | 0.02985% | 0.02985% | 0.02686% | 0.02686% | 0.02038% | 0.02038% | 0.01233% | 0.01233% | 0.006134% | 0.006134% | 0.002014% | 0.002014% | 0.0001984% | 0.0001984% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0009421% | 0.0009421% | 0.004214% | 0.004214% | 0.01004% | 0.01004% | 0.01463% | 0.01463% | 0.02175% | 0.02175% | 0.02632% | 0.02632% | 0.0263% | 0.0263% | 0.02494% | 0.02494% | 0.02143% | 0.02143% | 0.01893% | 0.01893% | 0.01603% | 0.01603% | 0.01163% | 0.01163% | 0.005995% | 0.005995% | 0.002536% | 0.002536% | 0.0003046% | 0.0003046% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-11 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0008854% | 0.0008854% | 0.004095% | 0.004095% | 0.008301% | 0.008301% | 0.01474% | 0.01474% | 0.02044% | 0.02044% | 0.02278% | 0.02278% | 0.02543% | 0.02543% | 0.02183% | 0.02183% | 0.01408% | 0.01408% | 0.0173% | 0.0173% | 0.01497% | 0.01497% | 0.01288% | 0.01288% | 0.007755% | 0.007755% | 0.002891% | 0.002891% | 0.0001489% | 0.0001489% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-12 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00114% | 0.00114% | 0.004737% | 0.004737% | 0.008877% | 0.008877% | 0.01293% | 0.01293% | 0.01971% | 0.01971% | 0.02424% | 0.02424% | 0.02414% | 0.02414% | 0.02038% | 0.02038% | 0.02303% | 0.02303% | 0.02183% | 0.02183% | 0.02154% | 0.02154% | 0.01401% | 0.01401% | 0.007813% | 0.007813% | 0.002467% | 0.002467% | 0.0003683% | 0.0003683% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-13 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001339% | 0.001339% | 0.004348% | 0.004348% | 0.00978% | 0.00978% | 0.01512% | 0.01512% | 0.0221% | 0.0221% | 0.02187% | 0.02187% | 0.02475% | 0.02475% | 0.02521% | 0.02521% | 0.02539% | 0.02539% | 0.02129% | 0.02129% | 0.01909% | 0.01909% | 0.01317% | 0.01317% | 0.007022% | 0.007022% | 0.003214% | 0.003214% | 0.0004747% | 0.0004747% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001119% | 0.001119% | 0.004078% | 0.004078% | 0.01026% | 0.01026% | 0.01416% | 0.01416% | 0.01862% | 0.01862% | 0.02347% | 0.02347% | 0.02508% | 0.02508% | 0.02651% | 0.02651% | 0.01893% | 0.01893% | 0.01626% | 0.01626% | 0.01658% | 0.01658% | 0.01332% | 0.01332% | 0.008117% | 0.008117% | 0.002678% | 0.002678% | 0.0004463% | 0.0004463% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-15 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001247% | 0.001247% | 0.004793% | 0.004793% | 0.01178% | 0.01178% | 0.01984% | 0.01984% | 0.02545% | 0.02545% | 0.02556% | 0.02556% | 0.02711% | 0.02711% | 0.02881% | 0.02881% | 0.02535% | 0.02535% | 0.02557% | 0.02557% | 0.02103% | 0.02103% | 0.01386% | 0.01386% | 0.00783% | 0.00783% | 0.002542% | 0.002542% | 0.0005738% | 0.0005738% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-16 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001544% | 0.001544% | 0.004204% | 0.004204% | 0.006455% | 0.006455% | 0.0124% | 0.0124% | 0.01861% | 0.01861% | 0.02336% | 0.02336% | 0.02118% | 0.02118% | 0.02608% | 0.02608% | 0.02638% | 0.02638% | 0.02139% | 0.02139% | 0.01686% | 0.01686% | 0.01501% | 0.01501% | 0.007524% | 0.007524% | 0.00328% | 0.00328% | 0.0004888% | 0.0004888% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-17 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001523% | 0.001523% | 0.005739% | 0.005739% | 0.01116% | 0.01116% | 0.01644% | 0.01644% | 0.02075% | 0.02075% | 0.02638% | 0.02638% | 0.02715% | 0.02715% | 0.02976% | 0.02976% | 0.02642% | 0.02642% | 0.01991% | 0.01991% | 0.01688% | 0.01688% | 0.01098% | 0.01098% | 0.007063% | 0.007063% | 0.00288% | 0.00288% | 0.0004818% | 0.0004818% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-18 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001332% | 0.001332% | 0.004427% | 0.004427% | 0.009929% | 0.009929% | 0.01537% | 0.01537% | 0.0204% | 0.0204% | 0.02194% | 0.02194% | 0.02234% | 0.02234% | 0.02179% | 0.02179% | 0.02058% | 0.02058% | 0.01817% | 0.01817% | 0.01524% | 0.01524% | 0.01363% | 0.01363% | 0.008485% | 0.008485% | 0.002857% | 0.002857% | 0.0004322% | 0.0004322% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-19 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001707% | 0.001707% | 0.006214% | 0.006214% | 0.01128% | 0.01128% | 0.01703% | 0.01703% | 0.02031% | 0.02031% | 0.02448% | 0.02448% | 0.02825% | 0.02825% | 0.03198% | 0.03198% | 0.02639% | 0.02639% | 0.02005% | 0.02005% | 0.01928% | 0.01928% | 0.01503% | 0.01503% | 0.008186% | 0.008186% | 0.003043% | 0.003043% | 0.0007013% | 0.0007013% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-20 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001757% | 0.001757% | 0.006594% | 0.006594% | 0.01396% | 0.01396% | 0.01933% | 0.01933% | 0.02224% | 0.02224% | 0.02221% | 0.02221% | 0.03108% | 0.03108% | 0.03369% | 0.03369% | 0.03037% | 0.03037% | 0.02211% | 0.02211% | 0.0205% | 0.0205% | 0.016% | 0.016% | 0.01014% | 0.01014% | 0.003568% | 0.003568% | 0.0007933% | 0.0007933% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-21 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001728% | 0.001728% | 0.005031% | 0.005031% | 0.01247% | 0.01247% | 0.01842% | 0.01842% | 0.02538% | 0.02538% | 0.02609% | 0.02609% | 0.02602% | 0.02602% | 0.02544% | 0.02544% | 0.02385% | 0.02385% | 0.02292% | 0.02292% | 0.0224% | 0.0224% | 0.0167% | 0.0167% | 0.00801% | 0.00801% | 0.003582% | 0.003582% | 0.0009492% | 0.0009492% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-22 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001742% | 0.001742% | 0.004552% | 0.004552% | 0.0108% | 0.0108% | 0.0188% | 0.0188% | 0.02636% | 0.02636% | 0.02635% | 0.02635% | 0.03581% | 0.03581% | 0.03116% | 0.03116% | 0.0266% | 0.0266% | 0.02372% | 0.02372% | 0.01922% | 0.01922% | 0.01438% | 0.01438% | 0.009037% | 0.009037% | 0.003108% | 0.003108% | 0.000758% | 0.000758% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001587% | 0.001587% | 0.005523% | 0.005523% | 0.01238% | 0.01238% | 0.01636% | 0.01636% | 0.02159% | 0.02159% | 0.02428% | 0.02428% | 0.0208% | 0.0208% | 0.01657% | 0.01657% | 0.01812% | 0.01812% | 0.01678% | 0.01678% | 0.009864% | 0.009864% | 0.01349% | 0.01349% | 0.008243% | 0.008243% | 0.003914% | 0.003914% | 0.0009917% | 0.0009917% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001445% | 0.001445% | 0.005431% | 0.005431% | 0.01162% | 0.01162% | 0.01748% | 0.01748% | 0.02704% | 0.02704% | 0.0258% | 0.0258% | 0.02673% | 0.02673% | 0.01758% | 0.01758% | 0.01886% | 0.01886% | 0.02077% | 0.02077% | 0.01517% | 0.01517% | 0.009784% | 0.009784% | 0.007462% | 0.007462% | 0.003678% | 0.003678% | 0.0007721% | 0.0007721% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-25 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001905% | 0.001905% | 0.005368% | 0.005368% | 0.01094% | 0.01094% | 0.01573% | 0.01573% | 0.02004% | 0.02004% | 0.02275% | 0.02275% | 0.02444% | 0.02444% | 0.02176% | 0.02176% | 0.0191% | 0.0191% | 0.01761% | 0.01761% | 0.01608% | 0.01608% | 0.01167% | 0.01167% | 0.006854% | 0.006854% | 0.003149% | 0.003149% | 0.0006447% | 0.0006447% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-26 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0017% | 0.0017% | 0.005941% | 0.005941% | 0.01201% | 0.01201% | 0.02023% | 0.02023% | 0.02946% | 0.02946% | 0.03592% | 0.03592% | 0.0367% | 0.0367% | 0.03503% | 0.03503% | 0.03354% | 0.03354% | 0.02988% | 0.02988% | 0.02419% | 0.02419% | 0.01539% | 0.01539% | 0.01035% | 0.01035% | 0.003762% | 0.003762% | 0.0009634% | 0.0009634% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-27 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001558% | 0.001558% | 0.006328% | 0.006328% | 0.01019% | 0.01019% | 0.01618% | 0.01618% | 0.02684% | 0.02684% | 0.03045% | 0.03045% | 0.03287% | 0.03287% | 0.02966% | 0.02966% | 0.03207% | 0.03207% | 0.02807% | 0.02807% | 0.022% | 0.022% | 0.01458% | 0.01458% | 0.008013% | 0.008013% | 0.003409% | 0.003409% | 0.0008643% | 0.0008643% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001764% | 0.001764% | 0.006181% | 0.006181% | 0.01235% | 0.01235% | 0.02054% | 0.02054% | 0.02662% | 0.02662% | 0.02767% | 0.02767% | 0.02972% | 0.02972% | 0.03703% | 0.03703% | 0.03271% | 0.03271% | 0.02515% | 0.02515% | 0.01949% | 0.01949% | 0.01433% | 0.01433% | 0.00843% | 0.00843% | 0.003951% | 0.003951% | 0.001147% | 0.001147% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-29 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00209% | 0.00209% | 0.005252% | 0.005252% | 0.01036% | 0.01036% | 0.01409% | 0.01409% | 0.01372% | 0.01372% | 0.01996% | 0.01996% | 0.01982% | 0.01982% | 0.0185% | 0.0185% | 0.01715% | 0.01715% | 0.01993% | 0.01993% | 0.0126% | 0.0126% | 0.01106% | 0.01106% | 0.007998% | 0.007998% | 0.003069% | 0.003069% | 0.000595% | 0.000595% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-30 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00175% | 0.00175% | 0.005232% | 0.005232% | 0.009006% | 0.009006% | 0.01272% | 0.01272% | 0.01704% | 0.01704% | 0.01723% | 0.01723% | 0.01844% | 0.01844% | 0.02321% | 0.02321% | 0.01812% | 0.01812% | 0.01695% | 0.01695% | 0.0163% | 0.0163% | 0.01146% | 0.01146% | 0.007976% | 0.007976% | 0.003576% | 0.003576% | 0.001303% | 0.001303% | 0% | 0% | 0% | 0% | 0% | 0%
2022-05-31 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001544% | 0.001544% | 0.004387% | 0.004387% | 0.007065% | 0.007065% | 0.01181% | 0.01181% | 0.01476% | 0.01476% | 0.01419% | 0.01419% | 0.01712% | 0.01712% | 0.01471% | 0.01471% | 0.01933% | 0.01933% | 0.01353% | 0.01353% | 0.01141% | 0.01141% | 0.01224% | 0.01224% | 0.006803% | 0.006803% | 0.003682% | 0.003682% | 0.001105% | 0.001105% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-01 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001714% | 0.001714% | 0.00487% | 0.00487% | 0.0107% | 0.0107% | 0.01572% | 0.01572% | 0.02026% | 0.02026% | 0.02665% | 0.02665% | 0.02053% | 0.02053% | 0.02485% | 0.02485% | 0.01774% | 0.01774% | 0.01739% | 0.01739% | 0.01518% | 0.01518% | 0.01316% | 0.01316% | 0.007633% | 0.007633% | 0.003419% | 0.003419% | 0.0009492% | 0.0009492% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-02 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00124% | 0.00124% | 0.003484% | 0.003484% | 0.006786% | 0.006786% | 0.01042% | 0.01042% | 0.01631% | 0.01631% | 0.0179% | 0.0179% | 0.0209% | 0.0209% | 0.01449% | 0.01449% | 0.01987% | 0.01987% | 0.01826% | 0.01826% | 0.01545% | 0.01545% | 0.01345% | 0.01345% | 0.008744% | 0.008744% | 0.003579% | 0.003579% | 0.001232% | 0.001232% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-03 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001806% | 0.001806% | 0.004896% | 0.004896% | 0.01128% | 0.01128% | 0.01374% | 0.01374% | 0.01766% | 0.01766% | 0.02039% | 0.02039% | 0.02605% | 0.02605% | 0.02333% | 0.02333% | 0.02144% | 0.02144% | 0.01892% | 0.01892% | 0.01492% | 0.01492% | 0.01101% | 0.01101% | 0.00822% | 0.00822% | 0.003152% | 0.003152% | 0.001105% | 0.001105% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-04 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001579% | 0.001579% | 0.004206% | 0.004206% | 0.007686% | 0.007686% | 0.01309% | 0.01309% | 0.01666% | 0.01666% | 0.02081% | 0.02081% | 0.02264% | 0.02264% | 0.02652% | 0.02652% | 0.01628% | 0.01628% | 0.01528% | 0.01528% | 0.01322% | 0.01322% | 0.01017% | 0.01017% | 0.006323% | 0.006323% | 0.003125% | 0.003125% | 0.001055% | 0.001055% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001976% | 0.001976% | 0.005037% | 0.005037% | 0.007554% | 0.007554% | 0.01236% | 0.01236% | 0.01802% | 0.01802% | 0.01602% | 0.01602% | 0.01965% | 0.01965% | 0.0239% | 0.0239% | 0.0262% | 0.0262% | 0.02369% | 0.02369% | 0.0186% | 0.0186% | 0.01261% | 0.01261% | 0.008449% | 0.008449% | 0.003875% | 0.003875% | 0.001225% | 0.001225% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-06 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 9.211e-05% | 9.211e-05% | 0.001828% | 0.001828% | 0.005491% | 0.005491% | 0.01218% | 0.01218% | 0.01772% | 0.01772% | 0.01991% | 0.01991% | 0.02226% | 0.02226% | 0.02564% | 0.02564% | 0.02915% | 0.02915% | 0.02701% | 0.02701% | 0.02703% | 0.02703% | 0.01874% | 0.01874% | 0.01627% | 0.01627% | 0.009593% | 0.009593% | 0.00376% | 0.00376% | 0.001204% | 0.001204% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-07 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0002126% | 0.0002126% | 0.002366% | 0.002366% | 0.006692% | 0.006692% | 0.01202% | 0.01202% | 0.01989% | 0.01989% | 0.02203% | 0.02203% | 0.02824% | 0.02824% | 0.02297% | 0.02297% | 0.02415% | 0.02415% | 0.01578% | 0.01578% | 0.01628% | 0.01628% | 0.0145% | 0.0145% | 0.01189% | 0.01189% | 0.00649% | 0.00649% | 0.003954% | 0.003954% | 0.0009067% | 0.0009067% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-08 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0002338% | 0.0002338% | 0.001806% | 0.001806% | 0.004882% | 0.004882% | 0.008889% | 0.008889% | 0.01484% | 0.01484% | 0.0175% | 0.0175% | 0.02282% | 0.02282% | 0.02057% | 0.02057% | 0.02341% | 0.02341% | 0.01656% | 0.01656% | 0.01198% | 0.01198% | 0.01642% | 0.01642% | 0.009522% | 0.009522% | 0.00736% | 0.00736% | 0.004243% | 0.004243% | 0.001232% | 0.001232% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-09 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0001842% | 0.0001842% | 0.002019% | 0.002019% | 0.00485% | 0.00485% | 0.01022% | 0.01022% | 0.01496% | 0.01496% | 0.02333% | 0.02333% | 0.0256% | 0.0256% | 0.03098% | 0.03098% | 0.02453% | 0.02453% | 0.02624% | 0.02624% | 0.02634% | 0.02634% | 0.01825% | 0.01825% | 0.01444% | 0.01444% | 0.00797% | 0.00797% | 0.002732% | 0.002732% | 0.001247% | 0.001247% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0001771% | 0.0001771% | 0.001473% | 0.001473% | 0.004102% | 0.004102% | 0.008488% | 0.008488% | 0.01371% | 0.01371% | 0.01675% | 0.01675% | 0.02455% | 0.02455% | 0.0263% | 0.0263% | 0.02632% | 0.02632% | 0.02559% | 0.02559% | 0.02648% | 0.02648% | 0.01939% | 0.01939% | 0.01304% | 0.01304% | 0.007997% | 0.007997% | 0.003338% | 0.003338% | 0.001147% | 0.001147% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-11 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0002197% | 0.0002197% | 0.001636% | 0.001636% | 0.004781% | 0.004781% | 0.009459% | 0.009459% | 0.01681% | 0.01681% | 0.02025% | 0.02025% | 0.02085% | 0.02085% | 0.03065% | 0.03065% | 0.02842% | 0.02842% | 0.02423% | 0.02423% | 0.01859% | 0.01859% | 0.02041% | 0.02041% | 0.01633% | 0.01633% | 0.009803% | 0.009803% | 0.003242% | 0.003242% | 0.001091% | 0.001091% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-12 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0001063% | 0.0001063% | 0.001629% | 0.001629% | 0.00406% | 0.00406% | 0.008318% | 0.008318% | 0.01093% | 0.01093% | 0.0127% | 0.0127% | 0.01089% | 0.01089% | 0.01318% | 0.01318% | 0.01184% | 0.01184% | 0.01247% | 0.01247% | 0.01496% | 0.01496% | 0.01147% | 0.01147% | 0.009373% | 0.009373% | 0.005015% | 0.005015% | 0.003101% | 0.003101% | 0.001275% | 0.001275% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-13 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0003897% | 0.0003897% | 0.001459% | 0.001459% | 0.004467% | 0.004467% | 0.00734% | 0.00734% | 0.01328% | 0.01328% | 0.01945% | 0.01945% | 0.0235% | 0.0235% | 0.01655% | 0.01655% | 0.01695% | 0.01695% | 0.02027% | 0.02027% | 0.0179% | 0.0179% | 0.01409% | 0.01409% | 0.01192% | 0.01192% | 0.006195% | 0.006195% | 0.003737% | 0.003737% | 0.00131% | 0.00131% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0002338% | 0.0002338% | 0.001828% | 0.001828% | 0.005247% | 0.005247% | 0.008718% | 0.008718% | 0.0125% | 0.0125% | 0.0142% | 0.0142% | 0.01455% | 0.01455% | 0.01834% | 0.01834% | 0.02112% | 0.02112% | 0.02341% | 0.02341% | 0.02441% | 0.02441% | 0.01808% | 0.01808% | 0.01406% | 0.01406% | 0.009304% | 0.009304% | 0.004396% | 0.004396% | 0.001693% | 0.001693% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-15 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0001913% | 0.0001913% | 0.001976% | 0.001976% | 0.006144% | 0.006144% | 0.0129% | 0.0129% | 0.02078% | 0.02078% | 0.02726% | 0.02726% | 0.03046% | 0.03046% | 0.02944% | 0.02944% | 0.02601% | 0.02601% | 0.01919% | 0.01919% | 0.01893% | 0.01893% | 0.01655% | 0.01655% | 0.01482% | 0.01482% | 0.009363% | 0.009363% | 0.004272% | 0.004272% | 0.001424% | 0.001424% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-16 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0002834% | 0.0002834% | 0.002309% | 0.002309% | 0.0056% | 0.0056% | 0.01013% | 0.01013% | 0.01618% | 0.01618% | 0.0208% | 0.0208% | 0.02365% | 0.02365% | 0.02018% | 0.02018% | 0.02135% | 0.02135% | 0.02545% | 0.02545% | 0.02521% | 0.02521% | 0.01399% | 0.01399% | 0.011% | 0.011% | 0.007713% | 0.007713% | 0.004291% | 0.004291% | 0.001636% | 0.001636% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-17 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0002196% | 0.0002196% | 0.00182% | 0.00182% | 0.004556% | 0.004556% | 0.008983% | 0.008983% | 0.01465% | 0.01465% | 0.01888% | 0.01888% | 0.02618% | 0.02618% | 0.02152% | 0.02152% | 0.01814% | 0.01814% | 0.0167% | 0.0167% | 0.01526% | 0.01526% | 0.01267% | 0.01267% | 0.01199% | 0.01199% | 0.005099% | 0.005099% | 0.002728% | 0.002728% | 0.0009917% | 0.0009917% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-18 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0002338% | 0.0002338% | 0.001742% | 0.001742% | 0.004958% | 0.004958% | 0.01094% | 0.01094% | 0.01407% | 0.01407% | 0.01887% | 0.01887% | 0.02122% | 0.02122% | 0.02458% | 0.02458% | 0.02416% | 0.02416% | 0.02734% | 0.02734% | 0.0195% | 0.0195% | 0.01958% | 0.01958% | 0.01422% | 0.01422% | 0.008742% | 0.008742% | 0.004555% | 0.004555% | 0.001374% | 0.001374% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-19 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0002126% | 0.0002126% | 0.001912% | 0.001912% | 0.005336% | 0.005336% | 0.009172% | 0.009172% | 0.01376% | 0.01376% | 0.02069% | 0.02069% | 0.02004% | 0.02004% | 0.02664% | 0.02664% | 0.02444% | 0.02444% | 0.0224% | 0.0224% | 0.02113% | 0.02113% | 0.01785% | 0.01785% | 0.01479% | 0.01479% | 0.009163% | 0.009163% | 0.003905% | 0.003905% | 0.001417% | 0.001417% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-20 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0001914% | 0.0001914% | 0.001452% | 0.001452% | 0.004584% | 0.004584% | 0.006572% | 0.006572% | 0.01151% | 0.01151% | 0.01159% | 0.01159% | 0.01645% | 0.01645% | 0.01575% | 0.01575% | 0.02302% | 0.02302% | 0.02392% | 0.02392% | 0.02318% | 0.02318% | 0.01935% | 0.01935% | 0.01623% | 0.01623% | 0.0107% | 0.0107% | 0.003725% | 0.003725% | 0.001282% | 0.001282% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-21 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 7.083e-05% | 7.083e-05% | 0.00153% | 0.00153% | 0.004456% | 0.004456% | 0.01103% | 0.01103% | 0.0141% | 0.0141% | 0.02296% | 0.02296% | 0.03015% | 0.03015% | 0.02934% | 0.02934% | 0.02864% | 0.02864% | 0.02639% | 0.02639% | 0.02749% | 0.02749% | 0.02185% | 0.02185% | 0.01733% | 0.01733% | 0.00885% | 0.00885% | 0.004585% | 0.004585% | 0.00187% | 0.00187% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-22 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0002976% | 0.0002976% | 0.002047% | 0.002047% | 0.005682% | 0.005682% | 0.009934% | 0.009934% | 0.01492% | 0.01492% | 0.01729% | 0.01729% | 0.02075% | 0.02075% | 0.02456% | 0.02456% | 0.02598% | 0.02598% | 0.02786% | 0.02786% | 0.02679% | 0.02679% | 0.02013% | 0.02013% | 0.0149% | 0.0149% | 0.01048% | 0.01048% | 0.004889% | 0.004889% | 0.001303% | 0.001303% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0003472% | 0.0003472% | 0.002118% | 0.002118% | 0.006017% | 0.006017% | 0.01168% | 0.01168% | 0.01635% | 0.01635% | 0.02083% | 0.02083% | 0.02336% | 0.02336% | 0.02556% | 0.02556% | 0.02685% | 0.02685% | 0.0236% | 0.0236% | 0.01963% | 0.01963% | 0.01879% | 0.01879% | 0.01364% | 0.01364% | 0.006932% | 0.006932% | 0.00417% | 0.00417% | 0.0009775% | 0.0009775% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0002267% | 0.0002267% | 0.002196% | 0.002196% | 0.006177% | 0.006177% | 0.01133% | 0.01133% | 0.01836% | 0.01836% | 0.02576% | 0.02576% | 0.02832% | 0.02832% | 0.0296% | 0.0296% | 0.02694% | 0.02694% | 0.02663% | 0.02663% | 0.02558% | 0.02558% | 0.02268% | 0.02268% | 0.01572% | 0.01572% | 0.00896% | 0.00896% | 0.003994% | 0.003994% | 0.0009633% | 0.0009633% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-25 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0003754% | 0.0003754% | 0.002132% | 0.002132% | 0.006194% | 0.006194% | 0.01289% | 0.01289% | 0.01977% | 0.01977% | 0.02522% | 0.02522% | 0.02565% | 0.02565% | 0.02947% | 0.02947% | 0.02957% | 0.02957% | 0.0243% | 0.0243% | 0.024% | 0.024% | 0.02144% | 0.02144% | 0.01672% | 0.01672% | 0.01124% | 0.01124% | 0.004924% | 0.004924% | 0.001693% | 0.001693% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-26 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0002551% | 0.0002551% | 0.001601% | 0.001601% | 0.004986% | 0.004986% | 0.01078% | 0.01078% | 0.01698% | 0.01698% | 0.02447% | 0.02447% | 0.03037% | 0.03037% | 0.03513% | 0.03513% | 0.03736% | 0.03736% | 0.03486% | 0.03486% | 0.02887% | 0.02887% | 0.02427% | 0.02427% | 0.01829% | 0.01829% | 0.01138% | 0.01138% | 0.004143% | 0.004143% | 0.0009491% | 0.0009491% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-27 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0001347% | 0.0001347% | 0.001332% | 0.001332% | 0.004388% | 0.004388% | 0.008203% | 0.008203% | 0.01355% | 0.01355% | 0.01519% | 0.01519% | 0.01888% | 0.01888% | 0.02167% | 0.02167% | 0.02339% | 0.02339% | 0.02723% | 0.02723% | 0.02015% | 0.02015% | 0.018% | 0.018% | 0.01377% | 0.01377% | 0.0083% | 0.0083% | 0.003712% | 0.003712% | 0.001098% | 0.001098% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.507e-05% | 8.507e-05% | 0.001962% | 0.001962% | 0.00523% | 0.00523% | 0.009318% | 0.009318% | 0.01334% | 0.01334% | 0.01867% | 0.01867% | 0.01866% | 0.01866% | 0.02054% | 0.02054% | 0.01585% | 0.01585% | 0.01768% | 0.01768% | 0.02259% | 0.02259% | 0.01582% | 0.01582% | 0.008047% | 0.008047% | 0.005349% | 0.005349% | 0.004287% | 0.004287% | 0.00114% | 0.00114% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-29 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001792% | 0.001792% | 0.006021% | 0.006021% | 0.01069% | 0.01069% | 0.01877% | 0.01877% | 0.02134% | 0.02134% | 0.02282% | 0.02282% | 0.02455% | 0.02455% | 0.02378% | 0.02378% | 0.02253% | 0.02253% | 0.02038% | 0.02038% | 0.01732% | 0.01732% | 0.01321% | 0.01321% | 0.00783% | 0.00783% | 0.00345% | 0.00345% | 0.001431% | 0.001431% | 0% | 0% | 0% | 0% | 0% | 0%
2022-06-30 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00182% | 0.00182% | 0.005502% | 0.005502% | 0.01106% | 0.01106% | 0.01572% | 0.01572% | 0.021% | 0.021% | 0.02584% | 0.02584% | 0.02831% | 0.02831% | 0.02671% | 0.02671% | 0.02263% | 0.02263% | 0.02138% | 0.02138% | 0.02015% | 0.02015% | 0.01412% | 0.01412% | 0.008208% | 0.008208% | 0.004626% | 0.004626% | 0.001487% | 0.001487% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-01 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002132% | 0.002132% | 0.005426% | 0.005426% | 0.01013% | 0.01013% | 0.01596% | 0.01596% | 0.02088% | 0.02088% | 0.01794% | 0.01794% | 0.01525% | 0.01525% | 0.02017% | 0.02017% | 0.0187% | 0.0187% | 0.02371% | 0.02371% | 0.0159% | 0.0159% | 0.01172% | 0.01172% | 0.008541% | 0.008541% | 0.004539% | 0.004539% | 0.0009563% | 0.0009563% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-02 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001742% | 0.001742% | 0.005706% | 0.005706% | 0.01354% | 0.01354% | 0.01624% | 0.01624% | 0.01912% | 0.01912% | 0.0222% | 0.0222% | 0.0294% | 0.0294% | 0.02471% | 0.02471% | 0.02718% | 0.02718% | 0.02565% | 0.02565% | 0.01995% | 0.01995% | 0.01665% | 0.01665% | 0.01016% | 0.01016% | 0.005109% | 0.005109% | 0.001551% | 0.001551% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-03 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002139% | 0.002139% | 0.005683% | 0.005683% | 0.01417% | 0.01417% | 0.01951% | 0.01951% | 0.02424% | 0.02424% | 0.02645% | 0.02645% | 0.0309% | 0.0309% | 0.0308% | 0.0308% | 0.02831% | 0.02831% | 0.02388% | 0.02388% | 0.02194% | 0.02194% | 0.01814% | 0.01814% | 0.01041% | 0.01041% | 0.004387% | 0.004387% | 0.001551% | 0.001551% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-04 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001778% | 0.001778% | 0.005398% | 0.005398% | 0.008099% | 0.008099% | 0.02003% | 0.02003% | 0.02303% | 0.02303% | 0.02526% | 0.02526% | 0.02029% | 0.02029% | 0.02117% | 0.02117% | 0.02223% | 0.02223% | 0.02052% | 0.02052% | 0.01538% | 0.01538% | 0.01026% | 0.01026% | 0.008418% | 0.008418% | 0.004223% | 0.004223% | 0.001537% | 0.001537% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001976% | 0.001976% | 0.004591% | 0.004591% | 0.008918% | 0.008918% | 0.01381% | 0.01381% | 0.01768% | 0.01768% | 0.02276% | 0.02276% | 0.0262% | 0.0262% | 0.03296% | 0.03296% | 0.0342% | 0.0342% | 0.02475% | 0.02475% | 0.02322% | 0.02322% | 0.01576% | 0.01576% | 0.008469% | 0.008469% | 0.004746% | 0.004746% | 0.00175% | 0.00175% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-06 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002267% | 0.002267% | 0.006274% | 0.006274% | 0.01285% | 0.01285% | 0.02076% | 0.02076% | 0.02407% | 0.02407% | 0.02793% | 0.02793% | 0.031% | 0.031% | 0.03036% | 0.03036% | 0.03227% | 0.03227% | 0.03089% | 0.03089% | 0.02585% | 0.02585% | 0.01808% | 0.01808% | 0.01056% | 0.01056% | 0.004296% | 0.004296% | 0.001523% | 0.001523% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-07 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001629% | 0.001629% | 0.005289% | 0.005289% | 0.01027% | 0.01027% | 0.017% | 0.017% | 0.02362% | 0.02362% | 0.02636% | 0.02636% | 0.02839% | 0.02839% | 0.0318% | 0.0318% | 0.02602% | 0.02602% | 0.02492% | 0.02492% | 0.01912% | 0.01912% | 0.01031% | 0.01031% | 0.008107% | 0.008107% | 0.004178% | 0.004178% | 0.001197% | 0.001197% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-08 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001516% | 0.001516% | 0.00392% | 0.00392% | 0.009111% | 0.009111% | 0.01107% | 0.01107% | 0.01533% | 0.01533% | 0.0171% | 0.0171% | 0.01719% | 0.01719% | 0.01627% | 0.01627% | 0.01939% | 0.01939% | 0.01632% | 0.01632% | 0.01682% | 0.01682% | 0.01526% | 0.01526% | 0.009947% | 0.009947% | 0.004343% | 0.004343% | 0.001438% | 0.001438% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-09 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001863% | 0.001863% | 0.004949% | 0.004949% | 0.009947% | 0.009947% | 0.0165% | 0.0165% | 0.02258% | 0.02258% | 0.02336% | 0.02336% | 0.02319% | 0.02319% | 0.01833% | 0.01833% | 0.01845% | 0.01845% | 0.01598% | 0.01598% | 0.017% | 0.017% | 0.01136% | 0.01136% | 0.006939% | 0.006939% | 0.004124% | 0.004124% | 0.001466% | 0.001466% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001622% | 0.001622% | 0.005187% | 0.005187% | 0.009586% | 0.009586% | 0.01557% | 0.01557% | 0.01839% | 0.01839% | 0.02236% | 0.02236% | 0.02007% | 0.02007% | 0.02192% | 0.02192% | 0.02298% | 0.02298% | 0.02345% | 0.02345% | 0.0215% | 0.0215% | 0.01701% | 0.01701% | 0.01072% | 0.01072% | 0.004994% | 0.004994% | 0.001395% | 0.001395% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-11 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001572% | 0.001572% | 0.004245% | 0.004245% | 0.008645% | 0.008645% | 0.01431% | 0.01431% | 0.0189% | 0.0189% | 0.01676% | 0.01676% | 0.02408% | 0.02408% | 0.01902% | 0.01902% | 0.02127% | 0.02127% | 0.01777% | 0.01777% | 0.0161% | 0.0161% | 0.01187% | 0.01187% | 0.008479% | 0.008479% | 0.004106% | 0.004106% | 0.001431% | 0.001431% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-12 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001502% | 0.001502% | 0.004188% | 0.004188% | 0.008208% | 0.008208% | 0.01316% | 0.01316% | 0.01462% | 0.01462% | 0.01929% | 0.01929% | 0.0161% | 0.0161% | 0.02085% | 0.02085% | 0.02117% | 0.02117% | 0.02095% | 0.02095% | 0.01618% | 0.01618% | 0.009614% | 0.009614% | 0.008355% | 0.008355% | 0.00405% | 0.00405% | 0.00153% | 0.00153% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-13 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001325% | 0.001325% | 0.004524% | 0.004524% | 0.01035% | 0.01035% | 0.01689% | 0.01689% | 0.0217% | 0.0217% | 0.02425% | 0.02425% | 0.02056% | 0.02056% | 0.02293% | 0.02293% | 0.01642% | 0.01642% | 0.01703% | 0.01703% | 0.02027% | 0.02027% | 0.01256% | 0.01256% | 0.006867% | 0.006867% | 0.0039% | 0.0039% | 0.001148% | 0.001148% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001749% | 0.001749% | 0.004844% | 0.004844% | 0.009591% | 0.009591% | 0.01374% | 0.01374% | 0.01806% | 0.01806% | 0.01884% | 0.01884% | 0.01604% | 0.01604% | 0.01477% | 0.01477% | 0.01796% | 0.01796% | 0.0148% | 0.0148% | 0.01478% | 0.01478% | 0.01028% | 0.01028% | 0.007416% | 0.007416% | 0.003481% | 0.003481% | 0.00119% | 0.00119% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-15 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00141% | 0.00141% | 0.004985% | 0.004985% | 0.01046% | 0.01046% | 0.01616% | 0.01616% | 0.01806% | 0.01806% | 0.01713% | 0.01713% | 0.0186% | 0.0186% | 0.02102% | 0.02102% | 0.02027% | 0.02027% | 0.0174% | 0.0174% | 0.01472% | 0.01472% | 0.00967% | 0.00967% | 0.006528% | 0.006528% | 0.002942% | 0.002942% | 0.0008288% | 0.0008288% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-16 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001615% | 0.001615% | 0.004194% | 0.004194% | 0.008152% | 0.008152% | 0.01294% | 0.01294% | 0.01645% | 0.01645% | 0.02044% | 0.02044% | 0.02013% | 0.02013% | 0.02126% | 0.02126% | 0.02284% | 0.02284% | 0.02347% | 0.02347% | 0.01738% | 0.01738% | 0.011% | 0.011% | 0.007134% | 0.007134% | 0.004065% | 0.004065% | 0.001112% | 0.001112% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-17 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00153% | 0.00153% | 0.004656% | 0.004656% | 0.01126% | 0.01126% | 0.01764% | 0.01764% | 0.02138% | 0.02138% | 0.02493% | 0.02493% | 0.02844% | 0.02844% | 0.02847% | 0.02847% | 0.02781% | 0.02781% | 0.02691% | 0.02691% | 0.0241% | 0.0241% | 0.01882% | 0.01882% | 0.01076% | 0.01076% | 0.004712% | 0.004712% | 0.001523% | 0.001523% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-18 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001679% | 0.001679% | 0.005596% | 0.005596% | 0.01139% | 0.01139% | 0.01781% | 0.01781% | 0.02457% | 0.02457% | 0.02566% | 0.02566% | 0.03276% | 0.03276% | 0.03409% | 0.03409% | 0.03232% | 0.03232% | 0.03116% | 0.03116% | 0.02182% | 0.02182% | 0.01562% | 0.01562% | 0.007702% | 0.007702% | 0.003316% | 0.003316% | 0.001225% | 0.001225% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-19 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001346% | 0.001346% | 0.004404% | 0.004404% | 0.008647% | 0.008647% | 0.0178% | 0.0178% | 0.02031% | 0.02031% | 0.02061% | 0.02061% | 0.02481% | 0.02481% | 0.01946% | 0.01946% | 0.0174% | 0.0174% | 0.01942% | 0.01942% | 0.01681% | 0.01681% | 0.01387% | 0.01387% | 0.008487% | 0.008487% | 0.0041% | 0.0041% | 0.001431% | 0.001431% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-20 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001211% | 0.001211% | 0.00398% | 0.00398% | 0.009356% | 0.009356% | 0.01364% | 0.01364% | 0.01849% | 0.01849% | 0.01225% | 0.01225% | 0.01803% | 0.01803% | 0.02093% | 0.02093% | 0.02088% | 0.02088% | 0.0225% | 0.0225% | 0.01673% | 0.01673% | 0.01364% | 0.01364% | 0.008705% | 0.008705% | 0.00384% | 0.00384% | 0.0009562% | 0.0009562% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-21 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001431% | 0.001431% | 0.005103% | 0.005103% | 0.01152% | 0.01152% | 0.01759% | 0.01759% | 0.02469% | 0.02469% | 0.02608% | 0.02608% | 0.03085% | 0.03085% | 0.02855% | 0.02855% | 0.02987% | 0.02987% | 0.02238% | 0.02238% | 0.01998% | 0.01998% | 0.0136% | 0.0136% | 0.009184% | 0.009184% | 0.003952% | 0.003952% | 0.001417% | 0.001417% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-22 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001247% | 0.001247% | 0.004346% | 0.004346% | 0.008728% | 0.008728% | 0.01722% | 0.01722% | 0.02105% | 0.02105% | 0.02509% | 0.02509% | 0.02313% | 0.02313% | 0.02026% | 0.02026% | 0.01504% | 0.01504% | 0.01088% | 0.01088% | 0.01221% | 0.01221% | 0.009559% | 0.009559% | 0.009598% | 0.009598% | 0.004348% | 0.004348% | 0.001325% | 0.001325% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001388% | 0.001388% | 0.005527% | 0.005527% | 0.0101% | 0.0101% | 0.01478% | 0.01478% | 0.02217% | 0.02217% | 0.0228% | 0.0228% | 0.02452% | 0.02452% | 0.01941% | 0.01941% | 0.02043% | 0.02043% | 0.02361% | 0.02361% | 0.0199% | 0.0199% | 0.01647% | 0.01647% | 0.01024% | 0.01024% | 0.00401% | 0.00401% | 0.00107% | 0.00107% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0009988% | 0.0009988% | 0.003611% | 0.003611% | 0.008503% | 0.008503% | 0.01315% | 0.01315% | 0.01514% | 0.01514% | 0.01559% | 0.01559% | 0.01594% | 0.01594% | 0.01655% | 0.01655% | 0.0135% | 0.0135% | 0.01133% | 0.01133% | 0.007012% | 0.007012% | 0.0106% | 0.0106% | 0.006607% | 0.006607% | 0.003012% | 0.003012% | 0.0007296% | 0.0007296% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-25 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001197% | 0.001197% | 0.00449% | 0.00449% | 0.00943% | 0.00943% | 0.01499% | 0.01499% | 0.02066% | 0.02066% | 0.0232% | 0.0232% | 0.02184% | 0.02184% | 0.02331% | 0.02331% | 0.01716% | 0.01716% | 0.01765% | 0.01765% | 0.01393% | 0.01393% | 0.01102% | 0.01102% | 0.007613% | 0.007613% | 0.004299% | 0.004299% | 0.001126% | 0.001126% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-26 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00131% | 0.00131% | 0.003741% | 0.003741% | 0.007013% | 0.007013% | 0.009825% | 0.009825% | 0.01513% | 0.01513% | 0.01682% | 0.01682% | 0.0193% | 0.0193% | 0.01863% | 0.01863% | 0.01833% | 0.01833% | 0.01659% | 0.01659% | 0.01354% | 0.01354% | 0.008194% | 0.008194% | 0.006494% | 0.006494% | 0.002828% | 0.002828% | 0.0008643% | 0.0008643% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-27 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0009987% | 0.0009987% | 0.003693% | 0.003693% | 0.006493% | 0.006493% | 0.01072% | 0.01072% | 0.01389% | 0.01389% | 0.01765% | 0.01765% | 0.01472% | 0.01472% | 0.01174% | 0.01174% | 0.0159% | 0.0159% | 0.01411% | 0.01411% | 0.01107% | 0.01107% | 0.009098% | 0.009098% | 0.005234% | 0.005234% | 0.002983% | 0.002983% | 0.0006376% | 0.0006376% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001211% | 0.001211% | 0.004926% | 0.004926% | 0.01073% | 0.01073% | 0.01592% | 0.01592% | 0.01293% | 0.01293% | 0.02404% | 0.02404% | 0.02429% | 0.02429% | 0.02201% | 0.02201% | 0.01872% | 0.01872% | 0.0177% | 0.0177% | 0.01315% | 0.01315% | 0.00953% | 0.00953% | 0.007735% | 0.007735% | 0.003753% | 0.003753% | 0.0009845% | 0.0009845% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-29 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001055% | 0.001055% | 0.003974% | 0.003974% | 0.00895% | 0.00895% | 0.01396% | 0.01396% | 0.01658% | 0.01658% | 0.01749% | 0.01749% | 0.01621% | 0.01621% | 0.02317% | 0.02317% | 0.02194% | 0.02194% | 0.01097% | 0.01097% | 0.01277% | 0.01277% | 0.00946% | 0.00946% | 0.005008% | 0.005008% | 0.003774% | 0.003774% | 0.0006375% | 0.0006375% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-30 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001077% | 0.001077% | 0.003629% | 0.003629% | 0.009947% | 0.009947% | 0.01507% | 0.01507% | 0.01684% | 0.01684% | 0.01695% | 0.01695% | 0.01865% | 0.01865% | 0.02481% | 0.02481% | 0.01891% | 0.01891% | 0.01474% | 0.01474% | 0.01572% | 0.01572% | 0.01011% | 0.01011% | 0.009286% | 0.009286% | 0.003166% | 0.003166% | 0.0007579% | 0.0007579% | 0% | 0% | 0% | 0% | 0% | 0%
2022-07-31 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001282% | 0.001282% | 0.005074% | 0.005074% | 0.01239% | 0.01239% | 0.02025% | 0.02025% | 0.02184% | 0.02184% | 0.0198% | 0.0198% | 0.02646% | 0.02646% | 0.02917% | 0.02917% | 0.02427% | 0.02427% | 0.02268% | 0.02268% | 0.01553% | 0.01553% | 0.01078% | 0.01078% | 0.007345% | 0.007345% | 0.003842% | 0.003842% | 0.0009208% | 0.0009208% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-01 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00114% | 0.00114% | 0.004689% | 0.004689% | 0.01078% | 0.01078% | 0.01777% | 0.01777% | 0.02244% | 0.02244% | 0.02622% | 0.02622% | 0.02261% | 0.02261% | 0.02927% | 0.02927% | 0.02472% | 0.02472% | 0.01687% | 0.01687% | 0.0186% | 0.0186% | 0.01371% | 0.01371% | 0.008566% | 0.008566% | 0.002614% | 0.002614% | 0.0006871% | 0.0006871% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-02 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0009775% | 0.0009775% | 0.003384% | 0.003384% | 0.007911% | 0.007911% | 0.01419% | 0.01419% | 0.01886% | 0.01886% | 0.02117% | 0.02117% | 0.02261% | 0.02261% | 0.02534% | 0.02534% | 0.02029% | 0.02029% | 0.02063% | 0.02063% | 0.01811% | 0.01811% | 0.01153% | 0.01153% | 0.006828% | 0.006828% | 0.003123% | 0.003123% | 0.0004958% | 0.0004958% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-03 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001006% | 0.001006% | 0.003507% | 0.003507% | 0.008581% | 0.008581% | 0.01485% | 0.01485% | 0.01841% | 0.01841% | 0.02202% | 0.02202% | 0.02102% | 0.02102% | 0.02203% | 0.02203% | 0.02538% | 0.02538% | 0.02276% | 0.02276% | 0.0177% | 0.0177% | 0.01246% | 0.01246% | 0.008898% | 0.008898% | 0.003306% | 0.003306% | 0.0005456% | 0.0005456% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-04 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00107% | 0.00107% | 0.004695% | 0.004695% | 0.01095% | 0.01095% | 0.01596% | 0.01596% | 0.0238% | 0.0238% | 0.02455% | 0.02455% | 0.01574% | 0.01574% | 0.01905% | 0.01905% | 0.02133% | 0.02133% | 0.02501% | 0.02501% | 0.0211% | 0.0211% | 0.01421% | 0.01421% | 0.009202% | 0.009202% | 0.00322% | 0.00322% | 0.0005668% | 0.0005668% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0005454% | 0.0005454% | 0.004348% | 0.004348% | 0.009414% | 0.009414% | 0.01664% | 0.01664% | 0.02616% | 0.02616% | 0.0274% | 0.0274% | 0.03035% | 0.03035% | 0.02375% | 0.02375% | 0.02456% | 0.02456% | 0.02591% | 0.02591% | 0.02001% | 0.02001% | 0.014% | 0.014% | 0.009055% | 0.009055% | 0.003342% | 0.003342% | 0.0005172% | 0.0005172% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-06 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0008642% | 0.0008642% | 0.003671% | 0.003671% | 0.008889% | 0.008889% | 0.0151% | 0.0151% | 0.02054% | 0.02054% | 0.02413% | 0.02413% | 0.02741% | 0.02741% | 0.0283% | 0.0283% | 0.03568% | 0.03568% | 0.02552% | 0.02552% | 0.02345% | 0.02345% | 0.01638% | 0.01638% | 0.009914% | 0.009914% | 0.00333% | 0.00333% | 0.0005737% | 0.0005737% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-07 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0008287% | 0.0008287% | 0.003934% | 0.003934% | 0.009383% | 0.009383% | 0.0144% | 0.0144% | 0.01999% | 0.01999% | 0.02532% | 0.02532% | 0.02556% | 0.02556% | 0.03265% | 0.03265% | 0.02123% | 0.02123% | 0.02177% | 0.02177% | 0.02121% | 0.02121% | 0.01119% | 0.01119% | 0.006869% | 0.006869% | 0.002603% | 0.002603% | 0.0002763% | 0.0002763% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-08 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0006942% | 0.0006942% | 0.003578% | 0.003578% | 0.009653% | 0.009653% | 0.01445% | 0.01445% | 0.02128% | 0.02128% | 0.01838% | 0.01838% | 0.0213% | 0.0213% | 0.02867% | 0.02867% | 0.02417% | 0.02417% | 0.01455% | 0.01455% | 0.01483% | 0.01483% | 0.01063% | 0.01063% | 0.005624% | 0.005624% | 0.002995% | 0.002995% | 0.000425% | 0.000425% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-09 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0006587% | 0.0006587% | 0.002701% | 0.002701% | 0.008067% | 0.008067% | 0.01346% | 0.01346% | 0.01648% | 0.01648% | 0.02041% | 0.02041% | 0.02452% | 0.02452% | 0.02227% | 0.02227% | 0.01516% | 0.01516% | 0.01282% | 0.01282% | 0.01166% | 0.01166% | 0.01083% | 0.01083% | 0.005639% | 0.005639% | 0.002794% | 0.002794% | 0.0003613% | 0.0003613% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0005879% | 0.0005879% | 0.003619% | 0.003619% | 0.007305% | 0.007305% | 0.01584% | 0.01584% | 0.01993% | 0.01993% | 0.01809% | 0.01809% | 0.01689% | 0.01689% | 0.01307% | 0.01307% | 0.02283% | 0.02283% | 0.01319% | 0.01319% | 0.01779% | 0.01779% | 0.01147% | 0.01147% | 0.007451% | 0.007451% | 0.002956% | 0.002956% | 0.0003329% | 0.0003329% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-11 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0006942% | 0.0006942% | 0.002629% | 0.002629% | 0.007962% | 0.007962% | 0.01507% | 0.01507% | 0.01972% | 0.01972% | 0.02618% | 0.02618% | 0.0303% | 0.0303% | 0.03297% | 0.03297% | 0.02689% | 0.02689% | 0.0172% | 0.0172% | 0.01549% | 0.01549% | 0.009552% | 0.009552% | 0.004631% | 0.004631% | 0.002045% | 0.002045% | 0.0001346% | 0.0001346% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-12 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00051% | 0.00051% | 0.002727% | 0.002727% | 0.008318% | 0.008318% | 0.01346% | 0.01346% | 0.01933% | 0.01933% | 0.02606% | 0.02606% | 0.02885% | 0.02885% | 0.02474% | 0.02474% | 0.02176% | 0.02176% | 0.01858% | 0.01858% | 0.01944% | 0.01944% | 0.01295% | 0.01295% | 0.01006% | 0.01006% | 0.003106% | 0.003106% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-13 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0003755% | 0.0003755% | 0.002729% | 0.002729% | 0.007152% | 0.007152% | 0.01235% | 0.01235% | 0.01571% | 0.01571% | 0.01856% | 0.01856% | 0.02154% | 0.02154% | 0.02% | 0.02% | 0.01688% | 0.01688% | 0.02035% | 0.02035% | 0.01591% | 0.01591% | 0.01331% | 0.01331% | 0.006943% | 0.006943% | 0.002487% | 0.002487% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0004392% | 0.0004392% | 0.002267% | 0.002267% | 0.005962% | 0.005962% | 0.01032% | 0.01032% | 0.01545% | 0.01545% | 0.01705% | 0.01705% | 0.01735% | 0.01735% | 0.01731% | 0.01731% | 0.02214% | 0.02214% | 0.01813% | 0.01813% | 0.01317% | 0.01317% | 0.008131% | 0.008131% | 0.005425% | 0.005425% | 0.002033% | 0.002033% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-15 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0003613% | 0.0003613% | 0.002825% | 0.002825% | 0.00788% | 0.00788% | 0.01164% | 0.01164% | 0.01787% | 0.01787% | 0.017% | 0.017% | 0.02396% | 0.02396% | 0.007974% | 0.007974% | 0.02148% | 0.02148% | 0.01773% | 0.01773% | 0.01524% | 0.01524% | 0.01299% | 0.01299% | 0.007604% | 0.007604% | 0.002363% | 0.002363% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-16 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0002621% | 0.0002621% | 0.002507% | 0.002507% | 0.006634% | 0.006634% | 0.01182% | 0.01182% | 0.0151% | 0.0151% | 0.01579% | 0.01579% | 0.01761% | 0.01761% | 0.01892% | 0.01892% | 0.0164% | 0.0164% | 0.01473% | 0.01473% | 0.01515% | 0.01515% | 0.01117% | 0.01117% | 0.007019% | 0.007019% | 0.002608% | 0.002608% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-17 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0001771% | 0.0001771% | 0.003663% | 0.003663% | 0.009622% | 0.009622% | 0.01469% | 0.01469% | 0.01856% | 0.01856% | 0.02552% | 0.02552% | 0.026% | 0.026% | 0.02836% | 0.02836% | 0.02845% | 0.02845% | 0.01635% | 0.01635% | 0.01758% | 0.01758% | 0.01371% | 0.01371% | 0.006464% | 0.006464% | 0.002039% | 0.002039% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-18 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002399% | 0.002399% | 0.007337% | 0.007337% | 0.01185% | 0.01185% | 0.01394% | 0.01394% | 0.01334% | 0.01334% | 0.01717% | 0.01717% | 0.01864% | 0.01864% | 0.01283% | 0.01283% | 0.008624% | 0.008624% | 0.008932% | 0.008932% | 0.008859% | 0.008859% | 0.005737% | 0.005737% | 0.00193% | 0.00193% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-19 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003265% | 0.003265% | 0.005707% | 0.005707% | 0.01129% | 0.01129% | 0.01285% | 0.01285% | 0.01283% | 0.01283% | 0.01015% | 0.01015% | 0.01265% | 0.01265% | 0.01528% | 0.01528% | 0.01092% | 0.01092% | 0.01015% | 0.01015% | 0.007475% | 0.007475% | 0.006192% | 0.006192% | 0.00198% | 0.00198% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-20 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002839% | 0.002839% | 0.007933% | 0.007933% | 0.01556% | 0.01556% | 0.01656% | 0.01656% | 0.02263% | 0.02263% | 0.02478% | 0.02478% | 0.01983% | 0.01983% | 0.02393% | 0.02393% | 0.01697% | 0.01697% | 0.01496% | 0.01496% | 0.009506% | 0.009506% | 0.004963% | 0.004963% | 0.002001% | 0.002001% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-21 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002416% | 0.002416% | 0.007289% | 0.007289% | 0.009511% | 0.009511% | 0.01466% | 0.01466% | 0.01399% | 0.01399% | 0.0166% | 0.0166% | 0.01877% | 0.01877% | 0.02154% | 0.02154% | 0.0209% | 0.0209% | 0.01858% | 0.01858% | 0.01294% | 0.01294% | 0.006685% | 0.006685% | 0.002018% | 0.002018% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-22 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003008% | 0.003008% | 0.007004% | 0.007004% | 0.01078% | 0.01078% | 0.01432% | 0.01432% | 0.01775% | 0.01775% | 0.01998% | 0.01998% | 0.02261% | 0.02261% | 0.02276% | 0.02276% | 0.02068% | 0.02068% | 0.01698% | 0.01698% | 0.01395% | 0.01395% | 0.007905% | 0.007905% | 0.001849% | 0.001849% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002519% | 0.002519% | 0.007171% | 0.007171% | 0.01274% | 0.01274% | 0.01263% | 0.01263% | 0.01291% | 0.01291% | 0.01415% | 0.01415% | 0.0173% | 0.0173% | 0.02215% | 0.02215% | 0.02187% | 0.02187% | 0.01715% | 0.01715% | 0.01265% | 0.01265% | 0.00648% | 0.00648% | 0.001755% | 0.001755% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002637% | 0.002637% | 0.008081% | 0.008081% | 0.01297% | 0.01297% | 0.01942% | 0.01942% | 0.01836% | 0.01836% | 0.02397% | 0.02397% | 0.02056% | 0.02056% | 0.01945% | 0.01945% | 0.01876% | 0.01876% | 0.01241% | 0.01241% | 0.007011% | 0.007011% | 0.003206% | 0.003206% | 0.001433% | 0.001433% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-25 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002874% | 0.002874% | 0.008321% | 0.008321% | 0.0144% | 0.0144% | 0.01966% | 0.01966% | 0.01839% | 0.01839% | 0.01779% | 0.01779% | 0.0206% | 0.0206% | 0.01966% | 0.01966% | 0.01208% | 0.01208% | 0.01491% | 0.01491% | 0.01399% | 0.01399% | 0.007999% | 0.007999% | 0.001741% | 0.001741% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-26 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002346% | 0.002346% | 0.008302% | 0.008302% | 0.0124% | 0.0124% | 0.01438% | 0.01438% | 0.0162% | 0.0162% | 0.0213% | 0.0213% | 0.02063% | 0.02063% | 0.02024% | 0.02024% | 0.01558% | 0.01558% | 0.01332% | 0.01332% | 0.01064% | 0.01064% | 0.005672% | 0.005672% | 0.001259% | 0.001259% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-27 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002546% | 0.002546% | 0.005852% | 0.005852% | 0.01089% | 0.01089% | 0.01632% | 0.01632% | 0.01744% | 0.01744% | 0.01964% | 0.01964% | 0.02218% | 0.02218% | 0.01614% | 0.01614% | 0.01676% | 0.01676% | 0.01657% | 0.01657% | 0.009081% | 0.009081% | 0.005452% | 0.005452% | 0.000865% | 0.000865% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002749% | 0.002749% | 0.007087% | 0.007087% | 0.01306% | 0.01306% | 0.01931% | 0.01931% | 0.02202% | 0.02202% | 0.02288% | 0.02288% | 0.02057% | 0.02057% | 0.01916% | 0.01916% | 0.01924% | 0.01924% | 0.01447% | 0.01447% | 0.009945% | 0.009945% | 0.005853% | 0.005853% | 0.001225% | 0.001225% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-29 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001145% | 0.001145% | 0.004304% | 0.004304% | 0.01073% | 0.01073% | 0.01581% | 0.01581% | 0.01646% | 0.01646% | 0.02139% | 0.02139% | 0.01293% | 0.01293% | 0.01806% | 0.01806% | 0.005371% | 0.005371% | 0.006724% | 0.006724% | 0.007528% | 0.007528% | 0.004548% | 0.004548% | 0.001185% | 0.001185% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-30 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001844% | 0.001844% | 0.005951% | 0.005951% | 0.01213% | 0.01213% | 0.01756% | 0.01756% | 0.0188% | 0.0188% | 0.01593% | 0.01593% | 0.01603% | 0.01603% | 0.01538% | 0.01538% | 0.01411% | 0.01411% | 0.01148% | 0.01148% | 0.007678% | 0.007678% | 0.005291% | 0.005291% | 0.001096% | 0.001096% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-08-31 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002417% | 0.002417% | 0.008166% | 0.008166% | 0.01432% | 0.01432% | 0.02178% | 0.02178% | 0.02011% | 0.02011% | 0.0174% | 0.0174% | 0.01821% | 0.01821% | 0.01802% | 0.01802% | 0.009011% | 0.009011% | 0.01025% | 0.01025% | 0.007905% | 0.007905% | 0.004905% | 0.004905% | 0.000833% | 0.000833% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-01 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002716% | 0.002716% | 0.009852% | 0.009852% | 0.01619% | 0.01619% | 0.02323% | 0.02323% | 0.02744% | 0.02744% | 0.02947% | 0.02947% | 0.0289% | 0.0289% | 0.02486% | 0.02486% | 0.02376% | 0.02376% | 0.0196% | 0.0196% | 0.01007% | 0.01007% | 0.004641% | 0.004641% | 0.0009489% | 0.0009489% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-02 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002727% | 0.002727% | 0.01004% | 0.01004% | 0.01806% | 0.01806% | 0.02356% | 0.02356% | 0.02281% | 0.02281% | 0.02408% | 0.02408% | 0.02057% | 0.02057% | 0.01963% | 0.01963% | 0.0198% | 0.0198% | 0.01347% | 0.01347% | 0.009014% | 0.009014% | 0.00437% | 0.00437% | 0.0006099% | 0.0006099% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-03 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002207% | 0.002207% | 0.007292% | 0.007292% | 0.01309% | 0.01309% | 0.01686% | 0.01686% | 0.01789% | 0.01789% | 0.01689% | 0.01689% | 0.01323% | 0.01323% | 0.01255% | 0.01255% | 0.009809% | 0.009809% | 0.01053% | 0.01053% | 0.007383% | 0.007383% | 0.003432% | 0.003432% | 0.0006655% | 0.0006655% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-04 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001946% | 0.001946% | 0.004987% | 0.004987% | 0.008709% | 0.008709% | 0.01056% | 0.01056% | 0.01402% | 0.01402% | 0.01411% | 0.01411% | 0.01133% | 0.01133% | 0.008512% | 0.008512% | 0.008697% | 0.008697% | 0.01083% | 0.01083% | 0.005457% | 0.005457% | 0.003411% | 0.003411% | 0.0006588% | 0.0006588% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001692% | 0.001692% | 0.004357% | 0.004357% | 0.007918% | 0.007918% | 0.01103% | 0.01103% | 0.01211% | 0.01211% | 0.0124% | 0.0124% | 0.008834% | 0.008834% | 0.01027% | 0.01027% | 0.009132% | 0.009132% | 0.009186% | 0.009186% | 0.006025% | 0.006025% | 0.004428% | 0.004428% | 0.0006022% | 0.0006022% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-06 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002223% | 0.002223% | 0.006033% | 0.006033% | 0.01493% | 0.01493% | 0.02271% | 0.02271% | 0.02294% | 0.02294% | 0.02295% | 0.02295% | 0.02097% | 0.02097% | 0.01874% | 0.01874% | 0.01302% | 0.01302% | 0.01602% | 0.01602% | 0.01012% | 0.01012% | 0.004818% | 0.004818% | 0.0005879% | 0.0005879% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-07 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002105% | 0.002105% | 0.007591% | 0.007591% | 0.01181% | 0.01181% | 0.01888% | 0.01888% | 0.02331% | 0.02331% | 0.02037% | 0.02037% | 0.02038% | 0.02038% | 0.01877% | 0.01877% | 0.01512% | 0.01512% | 0.01528% | 0.01528% | 0.01063% | 0.01063% | 0.004517% | 0.004517% | 0.0003684% | 0.0003684% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-08 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001133% | 0.001133% | 0.004939% | 0.004939% | 0.007215% | 0.007215% | 0.01235% | 0.01235% | 0.01533% | 0.01533% | 0.01654% | 0.01654% | 0.01986% | 0.01986% | 0.01902% | 0.01902% | 0.01147% | 0.01147% | 0.01257% | 0.01257% | 0.009706% | 0.009706% | 0.003832% | 0.003832% | 0.0003685% | 0.0003685% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-09 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001696% | 0.001696% | 0.007766% | 0.007766% | 0.01071% | 0.01071% | 0.01322% | 0.01322% | 0.01946% | 0.01946% | 0.01311% | 0.01311% | 0.01898% | 0.01898% | 0.01837% | 0.01837% | 0.01341% | 0.01341% | 0.01073% | 0.01073% | 0.01044% | 0.01044% | 0.003637% | 0.003637% | 0.0002196% | 0.0002196% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001625% | 0.001625% | 0.007648% | 0.007648% | 0.01503% | 0.01503% | 0.02014% | 0.02014% | 0.02014% | 0.02014% | 0.01969% | 0.01969% | 0.02379% | 0.02379% | 0.02198% | 0.02198% | 0.01817% | 0.01817% | 0.01378% | 0.01378% | 0.007851% | 0.007851% | 0.0037% | 0.0037% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-11 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00142% | 0.00142% | 0.006975% | 0.006975% | 0.01563% | 0.01563% | 0.02014% | 0.02014% | 0.02166% | 0.02166% | 0.02472% | 0.02472% | 0.02775% | 0.02775% | 0.02711% | 0.02711% | 0.02221% | 0.02221% | 0.01761% | 0.01761% | 0.009568% | 0.009568% | 0.00542% | 0.00542% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-12 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001084% | 0.001084% | 0.006088% | 0.006088% | 0.01305% | 0.01305% | 0.01522% | 0.01522% | 0.01899% | 0.01899% | 0.0206% | 0.0206% | 0.02095% | 0.02095% | 0.024% | 0.024% | 0.01529% | 0.01529% | 0.01238% | 0.01238% | 0.0106% | 0.0106% | 0.003995% | 0.003995% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-13 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001692% | 0.001692% | 0.008467% | 0.008467% | 0.01617% | 0.01617% | 0.02291% | 0.02291% | 0.0256% | 0.0256% | 0.03137% | 0.03137% | 0.03435% | 0.03435% | 0.02914% | 0.02914% | 0.0214% | 0.0214% | 0.021% | 0.021% | 0.01378% | 0.01378% | 0.005053% | 0.005053% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001511% | 0.001511% | 0.006651% | 0.006651% | 0.01312% | 0.01312% | 0.01735% | 0.01735% | 0.02223% | 0.02223% | 0.03046% | 0.03046% | 0.02283% | 0.02283% | 0.02637% | 0.02637% | 0.01858% | 0.01858% | 0.01242% | 0.01242% | 0.01111% | 0.01111% | 0.00449% | 0.00449% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-15 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001341% | 0.001341% | 0.007468% | 0.007468% | 0.01466% | 0.01466% | 0.02068% | 0.02068% | 0.02054% | 0.02054% | 0.02344% | 0.02344% | 0.02529% | 0.02529% | 0.02452% | 0.02452% | 0.0183% | 0.0183% | 0.01108% | 0.01108% | 0.00843% | 0.00843% | 0.003395% | 0.003395% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-16 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0008403% | 0.0008403% | 0.003562% | 0.003562% | 0.006887% | 0.006887% | 0.008776% | 0.008776% | 0.01079% | 0.01079% | 0.01033% | 0.01033% | 0.01561% | 0.01561% | 0.01516% | 0.01516% | 0.01325% | 0.01325% | 0.01156% | 0.01156% | 0.009716% | 0.009716% | 0.003745% | 0.003745% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-17 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0009204% | 0.0009204% | 0.004941% | 0.004941% | 0.01023% | 0.01023% | 0.01764% | 0.01764% | 0.02027% | 0.02027% | 0.02147% | 0.02147% | 0.02103% | 0.02103% | 0.02323% | 0.02323% | 0.02012% | 0.02012% | 0.014% | 0.014% | 0.009941% | 0.009941% | 0.003374% | 0.003374% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-18 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001013% | 0.001013% | 0.005613% | 0.005613% | 0.007847% | 0.007847% | 0.01206% | 0.01206% | 0.0169% | 0.0169% | 0.02195% | 0.02195% | 0.01927% | 0.01927% | 0.0185% | 0.0185% | 0.01318% | 0.01318% | 0.01225% | 0.01225% | 0.006483% | 0.006483% | 0.003051% | 0.003051% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-19 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0006187% | 0.0006187% | 0.004569% | 0.004569% | 0.00905% | 0.00905% | 0.01557% | 0.01557% | 0.02222% | 0.02222% | 0.02166% | 0.02166% | 0.01971% | 0.01971% | 0.02007% | 0.02007% | 0.01552% | 0.01552% | 0.01542% | 0.01542% | 0.008177% | 0.008177% | 0.002646% | 0.002646% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-20 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0007073% | 0.0007073% | 0.005742% | 0.005742% | 0.009132% | 0.009132% | 0.01369% | 0.01369% | 0.01541% | 0.01541% | 0.01981% | 0.01981% | 0.02019% | 0.02019% | 0.01595% | 0.01595% | 0.01284% | 0.01284% | 0.01033% | 0.01033% | 0.00823% | 0.00823% | 0.002192% | 0.002192% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-21 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0006622% | 0.0006622% | 0.004366% | 0.004366% | 0.009184% | 0.009184% | 0.01589% | 0.01589% | 0.01415% | 0.01415% | 0.01584% | 0.01584% | 0.01561% | 0.01561% | 0.01793% | 0.01793% | 0.01675% | 0.01675% | 0.01284% | 0.01284% | 0.006786% | 0.006786% | 0.003011% | 0.003011% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-22 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0006824% | 0.0006824% | 0.003971% | 0.003971% | 0.00937% | 0.00937% | 0.01664% | 0.01664% | 0.02026% | 0.02026% | 0.0184% | 0.0184% | 0.01021% | 0.01021% | 0.01488% | 0.01488% | 0.0123% | 0.0123% | 0.01508% | 0.01508% | 0.008312% | 0.008312% | 0.002467% | 0.002467% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0004308% | 0.0004308% | 0.004523% | 0.004523% | 0.009837% | 0.009837% | 0.01474% | 0.01474% | 0.01997% | 0.01997% | 0.01921% | 0.01921% | 0.019% | 0.019% | 0.02023% | 0.02023% | 0.01372% | 0.01372% | 0.0107% | 0.0107% | 0.006594% | 0.006594% | 0.002697% | 0.002697% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0005831% | 0.0005831% | 0.006873% | 0.006873% | 0.01441% | 0.01441% | 0.02182% | 0.02182% | 0.02875% | 0.02875% | 0.03148% | 0.03148% | 0.02418% | 0.02418% | 0.0225% | 0.0225% | 0.01636% | 0.01636% | 0.01124% | 0.01124% | 0.006152% | 0.006152% | 0.001774% | 0.001774% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-25 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0002965% | 0.0002965% | 0.00361% | 0.00361% | 0.01016% | 0.01016% | 0.01546% | 0.01546% | 0.02271% | 0.02271% | 0.01374% | 0.01374% | 0.01633% | 0.01633% | 0.01964% | 0.01964% | 0.01919% | 0.01919% | 0.0132% | 0.0132% | 0.008893% | 0.008893% | 0.002191% | 0.002191% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-26 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005602% | 0.005602% | 0.01364% | 0.01364% | 0.01945% | 0.01945% | 0.02006% | 0.02006% | 0.02384% | 0.02384% | 0.01707% | 0.01707% | 0.01697% | 0.01697% | 0.01675% | 0.01675% | 0.01234% | 0.01234% | 0.008121% | 0.008121% | 0.001883% | 0.001883% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-27 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.006177% | 0.006177% | 0.01076% | 0.01076% | 0.01486% | 0.01486% | 0.0168% | 0.0168% | 0.01622% | 0.01622% | 0.01997% | 0.01997% | 0.0186% | 0.0186% | 0.0139% | 0.0139% | 0.01089% | 0.01089% | 0.006372% | 0.006372% | 0.00166% | 0.00166% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005865% | 0.005865% | 0.01298% | 0.01298% | 0.01937% | 0.01937% | 0.02185% | 0.02185% | 0.02422% | 0.02422% | 0.02474% | 0.02474% | 0.02426% | 0.02426% | 0.02372% | 0.02372% | 0.01652% | 0.01652% | 0.007218% | 0.007218% | 0.001539% | 0.001539% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-29 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004353% | 0.004353% | 0.00794% | 0.00794% | 0.01159% | 0.01159% | 0.0152% | 0.0152% | 0.02131% | 0.02131% | 0.01926% | 0.01926% | 0.01833% | 0.01833% | 0.01618% | 0.01618% | 0.01236% | 0.01236% | 0.006734% | 0.006734% | 0.001413% | 0.001413% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-09-30 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005767% | 0.005767% | 0.01324% | 0.01324% | 0.01974% | 0.01974% | 0.0232% | 0.0232% | 0.01033% | 0.01033% | 0.0146% | 0.0146% | 0.01399% | 0.01399% | 0.01367% | 0.01367% | 0.01231% | 0.01231% | 0.005885% | 0.005885% | 0.001237% | 0.001237% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-01 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004132% | 0.004132% | 0.00987% | 0.00987% | 0.01218% | 0.01218% | 0.01431% | 0.01431% | 0.01698% | 0.01698% | 0.01716% | 0.01716% | 0.02378% | 0.02378% | 0.01873% | 0.01873% | 0.01236% | 0.01236% | 0.005212% | 0.005212% | 0.0008229% | 0.0008229% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-02 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00432% | 0.00432% | 0.008167% | 0.008167% | 0.0151% | 0.0151% | 0.01652% | 0.01652% | 0.01712% | 0.01712% | 0.01915% | 0.01915% | 0.01198% | 0.01198% | 0.01105% | 0.01105% | 0.01126% | 0.01126% | 0.006805% | 0.006805% | 0.0006093% | 0.0006093% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-03 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005029% | 0.005029% | 0.01097% | 0.01097% | 0.01297% | 0.01297% | 0.01438% | 0.01438% | 0.0137% | 0.0137% | 0.01826% | 0.01826% | 0.01547% | 0.01547% | 0.01426% | 0.01426% | 0.01016% | 0.01016% | 0.006195% | 0.006195% | 0.0005954% | 0.0005954% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-04 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003933% | 0.003933% | 0.01068% | 0.01068% | 0.01343% | 0.01343% | 0.01249% | 0.01249% | 0.01841% | 0.01841% | 0.01821% | 0.01821% | 0.01663% | 0.01663% | 0.01371% | 0.01371% | 0.01098% | 0.01098% | 0.005775% | 0.005775% | 0.0004318% | 0.0004318% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002498% | 0.002498% | 0.007719% | 0.007719% | 0.01269% | 0.01269% | 0.01926% | 0.01926% | 0.02627% | 0.02627% | 0.02318% | 0.02318% | 0.01976% | 0.01976% | 0.01703% | 0.01703% | 0.01174% | 0.01174% | 0.005829% | 0.005829% | 0.0002073% | 0.0002073% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-06 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004039% | 0.004039% | 0.01011% | 0.01011% | 0.008738% | 0.008738% | 0.01405% | 0.01405% | 0.0171% | 0.0171% | 0.01598% | 0.01598% | 0.01881% | 0.01881% | 0.01421% | 0.01421% | 0.01156% | 0.01156% | 0.003708% | 0.003708% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-07 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002471% | 0.002471% | 0.005131% | 0.005131% | 0.008994% | 0.008994% | 0.0133% | 0.0133% | 0.01173% | 0.01173% | 0.01253% | 0.01253% | 0.01394% | 0.01394% | 0.009204% | 0.009204% | 0.007317% | 0.007317% | 0.004167% | 0.004167% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-08 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003263% | 0.003263% | 0.007559% | 0.007559% | 0.01262% | 0.01262% | 0.01501% | 0.01501% | 0.01709% | 0.01709% | 0.01604% | 0.01604% | 0.01005% | 0.01005% | 0.008946% | 0.008946% | 0.007816% | 0.007816% | 0.003456% | 0.003456% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-09 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004904% | 0.004904% | 0.01297% | 0.01297% | 0.01945% | 0.01945% | 0.02519% | 0.02519% | 0.01716% | 0.01716% | 0.01517% | 0.01517% | 0.01572% | 0.01572% | 0.01115% | 0.01115% | 0.008062% | 0.008062% | 0.00526% | 0.00526% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004507% | 0.004507% | 0.009669% | 0.009669% | 0.01665% | 0.01665% | 0.01875% | 0.01875% | 0.01962% | 0.01962% | 0.0146% | 0.0146% | 0.01295% | 0.01295% | 0.01077% | 0.01077% | 0.01157% | 0.01157% | 0.00557% | 0.00557% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-11 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004459% | 0.004459% | 0.009779% | 0.009779% | 0.01442% | 0.01442% | 0.01726% | 0.01726% | 0.01785% | 0.01785% | 0.0146% | 0.0146% | 0.01291% | 0.01291% | 0.01358% | 0.01358% | 0.01205% | 0.01205% | 0.004054% | 0.004054% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-12 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003405% | 0.003405% | 0.005269% | 0.005269% | 0.01418% | 0.01418% | 0.01586% | 0.01586% | 0.01271% | 0.01271% | 0.01418% | 0.01418% | 0.01639% | 0.01639% | 0.01441% | 0.01441% | 0.009103% | 0.009103% | 0.00443% | 0.00443% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-13 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004288% | 0.004288% | 0.00833% | 0.00833% | 0.008891% | 0.008891% | 0.008942% | 0.008942% | 0.01405% | 0.01405% | 0.007497% | 0.007497% | 0.01266% | 0.01266% | 0.007639% | 0.007639% | 0.006193% | 0.006193% | 0.002314% | 0.002314% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002903% | 0.002903% | 0.008824% | 0.008824% | 0.01315% | 0.01315% | 0.01586% | 0.01586% | 0.01049% | 0.01049% | 0.008755% | 0.008755% | 0.008467% | 0.008467% | 0.006478% | 0.006478% | 0.006089% | 0.006089% | 0.00174% | 0.00174% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-15 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002623% | 0.002623% | 0.004828% | 0.004828% | 0.005716% | 0.005716% | 0.007453% | 0.007453% | 0.01155% | 0.01155% | 0.01164% | 0.01164% | 0.01214% | 0.01214% | 0.006254% | 0.006254% | 0.00529% | 0.00529% | 0.002302% | 0.002302% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-16 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001256% | 0.001256% | 0.005909% | 0.005909% | 0.007101% | 0.007101% | 0.01363% | 0.01363% | 0.01772% | 0.01772% | 0.01343% | 0.01343% | 0.01109% | 0.01109% | 0.007246% | 0.007246% | 0.004393% | 0.004393% | 0.001961% | 0.001961% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-17 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00228% | 0.00228% | 0.004148% | 0.004148% | 0.006916% | 0.006916% | 0.007578% | 0.007578% | 0.005445% | 0.005445% | 0.003777% | 0.003777% | 0.01551% | 0.01551% | 0.009757% | 0.009757% | 0.00481% | 0.00481% | 0.002402% | 0.002402% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-18 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001301% | 0.001301% | 0.004922% | 0.004922% | 0.007227% | 0.007227% | 0.01116% | 0.01116% | 0.01443% | 0.01443% | 0.01151% | 0.01151% | 0.00947% | 0.00947% | 0.00942% | 0.00942% | 0.005575% | 0.005575% | 0.002551% | 0.002551% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-19 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001626% | 0.001626% | 0.006424% | 0.006424% | 0.005226% | 0.005226% | 0.0112% | 0.0112% | 0.01411% | 0.01411% | 0.01631% | 0.01631% | 0.01106% | 0.01106% | 0.009424% | 0.009424% | 0.006452% | 0.006452% | 0.00202% | 0.00202% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-20 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001419% | 0.001419% | 0.004899% | 0.004899% | 0.006972% | 0.006972% | 0.01109% | 0.01109% | 0.01482% | 0.01482% | 0.01626% | 0.01626% | 0.01939% | 0.01939% | 0.01507% | 0.01507% | 0.01201% | 0.01201% | 0.00387% | 0.00387% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-21 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001677% | 0.001677% | 0.004371% | 0.004371% | 0.01004% | 0.01004% | 0.009136% | 0.009136% | 0.01629% | 0.01629% | 0.01115% | 0.01115% | 0.01348% | 0.01348% | 0.01009% | 0.01009% | 0.007362% | 0.007362% | 0.002519% | 0.002519% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-22 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002743% | 0.002743% | 0.007378% | 0.007378% | 0.008422% | 0.008422% | 0.01206% | 0.01206% | 0.0172% | 0.0172% | 0.01628% | 0.01628% | 0.01075% | 0.01075% | 0.008098% | 0.008098% | 0.007977% | 0.007977% | 0.00173% | 0.00173% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001341% | 0.001341% | 0.007122% | 0.007122% | 0.009943% | 0.009943% | 0.01094% | 0.01094% | 0.01229% | 0.01229% | 0.01147% | 0.01147% | 0.009696% | 0.009696% | 0.008709% | 0.008709% | 0.004741% | 0.004741% | 0.002035% | 0.002035% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0007725% | 0.0007725% | 0.00281% | 0.00281% | 0.00677% | 0.00677% | 0.007545% | 0.007545% | 0.01049% | 0.01049% | 0.01086% | 0.01086% | 0.01013% | 0.01013% | 0.005924% | 0.005924% | 0.005064% | 0.005064% | 0.0008371% | 0.0008371% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-25 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.000168% | 0.000168% | 0.002094% | 0.002094% | 0.009704% | 0.009704% | 0.009754% | 0.009754% | 0.01662% | 0.01662% | 0.02182% | 0.02182% | 0.01801% | 0.01801% | 0.01529% | 0.01529% | 0.01255% | 0.01255% | 0.007461% | 0.007461% | 0.001017% | 0.001017% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-26 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0003941% | 0.0003941% | 0.004661% | 0.004661% | 0.007187% | 0.007187% | 0.005949% | 0.005949% | 0.01047% | 0.01047% | 0.009198% | 0.009198% | 0.01195% | 0.01195% | 0.01729% | 0.01729% | 0.008633% | 0.008633% | 0.004374% | 0.004374% | 0.0007907% | 0.0007907% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-27 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0002213% | 0.0002213% | 0.001515% | 0.001515% | 0.006629% | 0.006629% | 0.01416% | 0.01416% | 0.01844% | 0.01844% | 0.02117% | 0.02117% | 0.0194% | 0.0194% | 0.01217% | 0.01217% | 0.009728% | 0.009728% | 0.003477% | 0.003477% | 0.0005831% | 0.0005831% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0001925% | 0.0001925% | 0.002267% | 0.002267% | 0.006353% | 0.006353% | 0.01209% | 0.01209% | 0.01836% | 0.01836% | 0.01746% | 0.01746% | 0.01442% | 0.01442% | 0.01182% | 0.01182% | 0.006251% | 0.006251% | 0.002919% | 0.002919% | 0.0001851% | 0.0001851% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-29 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0005711% | 0.0005711% | 0.005328% | 0.005328% | 0.006912% | 0.006912% | 0.008448% | 0.008448% | 0.009634% | 0.009634% | 0.01089% | 0.01089% | 0.01178% | 0.01178% | 0.00907% | 0.00907% | 0.004865% | 0.004865% | 0.0007426% | 0.0007426% | 0.0001502% | 0.0001502% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-30 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0001406% | 0.0001406% | 0.003724% | 0.003724% | 0.005085% | 0.005085% | 0.008857% | 0.008857% | 0.008851% | 0.008851% | 0.01141% | 0.01141% | 0.008514% | 0.008514% | 0.004745% | 0.004745% | 0.003502% | 0.003502% | 0.0009055% | 0.0009055% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-10-31 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002435% | 0.002435% | 0.007303% | 0.007303% | 0.01465% | 0.01465% | 0.01657% | 0.01657% | 0.01842% | 0.01842% | 0.01519% | 0.01519% | 0.01101% | 0.01101% | 0.007801% | 0.007801% | 0.001201% | 0.001201% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-01 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003794% | 0.003794% | 0.00444% | 0.00444% | 0.008228% | 0.008228% | 0.008264% | 0.008264% | 0.01032% | 0.01032% | 0.01114% | 0.01114% | 0.008579% | 0.008579% | 0.0053% | 0.0053% | 0.0004187% | 0.0004187% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-02 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.008005% | 0.008005% | 0.01312% | 0.01312% | 0.0159% | 0.0159% | 0.01981% | 0.01981% | 0.01937% | 0.01937% | 0.01545% | 0.01545% | 0.01419% | 0.01419% | 0.01004% | 0.01004% | 0.0002073% | 0.0002073% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-03 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0059% | 0.0059% | 0.01082% | 0.01082% | 0.0223% | 0.0223% | 0.02043% | 0.02043% | 0.01546% | 0.01546% | 0.01236% | 0.01236% | 0.01008% | 0.01008% | 0.009482% | 0.009482% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-04 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003832% | 0.003832% | 0.008489% | 0.008489% | 0.01135% | 0.01135% | 0.01674% | 0.01674% | 0.01026% | 0.01026% | 0.009093% | 0.009093% | 0.00953% | 0.00953% | 0.004148% | 0.004148% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004788% | 0.004788% | 0.007456% | 0.007456% | 0.01149% | 0.01149% | 0.01367% | 0.01367% | 0.008197% | 0.008197% | 0.01201% | 0.01201% | 0.009071% | 0.009071% | 0.004379% | 0.004379% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-06 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.006716% | 0.006716% | 0.00901% | 0.00901% | 0.01274% | 0.01274% | 0.01771% | 0.01771% | 0.01468% | 0.01468% | 0.01032% | 0.01032% | 0.006083% | 0.006083% | 0.005728% | 0.005728% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-07 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003454% | 0.003454% | 0.007485% | 0.007485% | 0.01191% | 0.01191% | 0.01309% | 0.01309% | 0.009321% | 0.009321% | 0.009546% | 0.009546% | 0.008166% | 0.008166% | 0.003133% | 0.003133% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-08 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004976% | 0.004976% | 0.01132% | 0.01132% | 0.01704% | 0.01704% | 0.01172% | 0.01172% | 0.00885% | 0.00885% | 0.006989% | 0.006989% | 0.00538% | 0.00538% | 0.003114% | 0.003114% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-09 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002921% | 0.002921% | 0.005871% | 0.005871% | 0.0115% | 0.0115% | 0.0066% | 0.0066% | 0.01037% | 0.01037% | 0.00803% | 0.00803% | 0.01055% | 0.01055% | 0.004988% | 0.004988% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.006134% | 0.006134% | 0.008701% | 0.008701% | 0.01301% | 0.01301% | 0.0146% | 0.0146% | 0.01287% | 0.01287% | 0.01259% | 0.01259% | 0.008108% | 0.008108% | 0.003873% | 0.003873% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-11 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00295% | 0.00295% | 0.008349% | 0.008349% | 0.01226% | 0.01226% | 0.01403% | 0.01403% | 0.01338% | 0.01338% | 0.01199% | 0.01199% | 0.007197% | 0.007197% | 0.004911% | 0.004911% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-12 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004338% | 0.004338% | 0.008991% | 0.008991% | 0.01387% | 0.01387% | 0.01378% | 0.01378% | 0.01328% | 0.01328% | 0.01086% | 0.01086% | 0.006433% | 0.006433% | 0.006067% | 0.006067% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-13 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005985% | 0.005985% | 0.0104% | 0.0104% | 0.01393% | 0.01393% | 0.02163% | 0.02163% | 0.01879% | 0.01879% | 0.01265% | 0.01265% | 0.01466% | 0.01466% | 0.008963% | 0.008963% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002109% | 0.002109% | 0.004219% | 0.004219% | 0.006367% | 0.006367% | 0.008386% | 0.008386% | 0.008521% | 0.008521% | 0.007618% | 0.007618% | 0.004391% | 0.004391% | 0.002489% | 0.002489% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-15 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002996% | 0.002996% | 0.002355% | 0.002355% | 0.005267% | 0.005267% | 0.005554% | 0.005554% | 0.009313% | 0.009313% | 0.007678% | 0.007678% | 0.005062% | 0.005062% | 0.002457% | 0.002457% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-16 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00221% | 0.00221% | 0.003861% | 0.003861% | 0.01181% | 0.01181% | 0.01015% | 0.01015% | 0.01481% | 0.01481% | 0.008343% | 0.008343% | 0.005237% | 0.005237% | 0.003555% | 0.003555% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-17 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0029% | 0.0029% | 0.00973% | 0.00973% | 0.01051% | 0.01051% | 0.01431% | 0.01431% | 0.01709% | 0.01709% | 0.01185% | 0.01185% | 0.007952% | 0.007952% | 0.005832% | 0.005832% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-18 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004845% | 0.004845% | 0.009744% | 0.009744% | 0.01554% | 0.01554% | 0.01595% | 0.01595% | 0.01594% | 0.01594% | 0.01108% | 0.01108% | 0.008089% | 0.008089% | 0.003333% | 0.003333% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-19 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002457% | 0.002457% | 0.007328% | 0.007328% | 0.009845% | 0.009845% | 0.01064% | 0.01064% | 0.01267% | 0.01267% | 0.008068% | 0.008068% | 0.01085% | 0.01085% | 0.004828% | 0.004828% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-20 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001628% | 0.001628% | 0.003035% | 0.003035% | 0.005541% | 0.005541% | 0.003883% | 0.003883% | 0.006172% | 0.006172% | 0.007248% | 0.007248% | 0.004354% | 0.004354% | 0.001934% | 0.001934% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-21 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001257% | 0.001257% | 0.003126% | 0.003126% | 0.007602% | 0.007602% | 0.01158% | 0.01158% | 0.008956% | 0.008956% | 0.007565% | 0.007565% | 0.008962% | 0.008962% | 0.004533% | 0.004533% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-22 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002487% | 0.002487% | 0.006835% | 0.006835% | 0.01446% | 0.01446% | 0.01879% | 0.01879% | 0.01456% | 0.01456% | 0.01374% | 0.01374% | 0.008585% | 0.008585% | 0.005196% | 0.005196% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002178% | 0.002178% | 0.004793% | 0.004793% | 0.01238% | 0.01238% | 0.01544% | 0.01544% | 0.01394% | 0.01394% | 0.01066% | 0.01066% | 0.006818% | 0.006818% | 0.005144% | 0.005144% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00169% | 0.00169% | 0.004918% | 0.004918% | 0.005697% | 0.005697% | 0.004914% | 0.004914% | 0.006198% | 0.006198% | 0.007683% | 0.007683% | 0.005726% | 0.005726% | 0.001497% | 0.001497% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-25 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002209% | 0.002209% | 0.006092% | 0.006092% | 0.00956% | 0.00956% | 0.01161% | 0.01161% | 0.01357% | 0.01357% | 0.01239% | 0.01239% | 0.008115% | 0.008115% | 0.002626% | 0.002626% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-26 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002166% | 0.002166% | 0.008019% | 0.008019% | 0.01145% | 0.01145% | 0.01477% | 0.01477% | 0.01066% | 0.01066% | 0.007685% | 0.007685% | 0.00538% | 0.00538% | 0.003041% | 0.003041% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-27 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0008693% | 0.0008693% | 0.003817% | 0.003817% | 0.006582% | 0.006582% | 0.00788% | 0.00788% | 0.006481% | 0.006481% | 0.005684% | 0.005684% | 0.003143% | 0.003143% | 0.00356% | 0.00356% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001332% | 0.001332% | 0.005939% | 0.005939% | 0.0128% | 0.0128% | 0.01066% | 0.01066% | 0.01164% | 0.01164% | 0.01048% | 0.01048% | 0.007588% | 0.007588% | 0.003077% | 0.003077% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-29 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0008757% | 0.0008757% | 0.00382% | 0.00382% | 0.006805% | 0.006805% | 0.008618% | 0.008618% | 0.008326% | 0.008326% | 0.007491% | 0.007491% | 0.005471% | 0.005471% | 0.002154% | 0.002154% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-11-30 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001133% | 0.001133% | 0.007225% | 0.007225% | 0.01251% | 0.01251% | 0.01236% | 0.01236% | 0.01245% | 0.01245% | 0.009172% | 0.009172% | 0.0054% | 0.0054% | 0.003102% | 0.003102% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-01 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0003748% | 0.0003748% | 0.006712% | 0.006712% | 0.007866% | 0.007866% | 0.01021% | 0.01021% | 0.01389% | 0.01389% | 0.0141% | 0.0141% | 0.0102% | 0.0102% | 0.00318% | 0.00318% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-02 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0001111% | 0.0001111% | 0.001746% | 0.001746% | 0.004989% | 0.004989% | 0.006792% | 0.006792% | 0.009832% | 0.009832% | 0.00796% | 0.00796% | 0.005318% | 0.005318% | 0.002585% | 0.002585% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-03 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004013% | 0.004013% | 0.006116% | 0.006116% | 0.003724% | 0.003724% | 0.008456% | 0.008456% | 0.004103% | 0.004103% | 0.003209% | 0.003209% | 0.001497% | 0.001497% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-04 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00792% | 0.00792% | 0.01246% | 0.01246% | 0.01528% | 0.01528% | 0.01431% | 0.01431% | 0.01114% | 0.01114% | 0.005338% | 0.005338% | 0.001602% | 0.001602% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005968% | 0.005968% | 0.0088% | 0.0088% | 0.009403% | 0.009403% | 0.008982% | 0.008982% | 0.006584% | 0.006584% | 0.00394% | 0.00394% | 0.001276% | 0.001276% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-06 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00242% | 0.00242% | 0.002658% | 0.002658% | 0.004104% | 0.004104% | 0.004595% | 0.004595% | 0.004456% | 0.004456% | 0.004587% | 0.004587% | 0.0009164% | 0.0009164% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-07 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002217% | 0.002217% | 0.006856% | 0.006856% | 0.005896% | 0.005896% | 0.005455% | 0.005455% | 0.009588% | 0.009588% | 0.009079% | 0.009079% | 0.002156% | 0.002156% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-08 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.006086% | 0.006086% | 0.008945% | 0.008945% | 0.0109% | 0.0109% | 0.007094% | 0.007094% | 0.009469% | 0.009469% | 0.008227% | 0.008227% | 0.003527% | 0.003527% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-09 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005957% | 0.005957% | 0.01163% | 0.01163% | 0.01201% | 0.01201% | 0.01564% | 0.01564% | 0.015% | 0.015% | 0.008848% | 0.008848% | 0.004036% | 0.004036% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0009692% | 0.0009692% | 0.002092% | 0.002092% | 0.001784% | 0.001784% | 0.004097% | 0.004097% | 0.003313% | 0.003313% | 0.002499% | 0.002499% | 0.0008597% | 0.0008597% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-11 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.00548% | 0.00548% | 0.009426% | 0.009426% | 0.01063% | 0.01063% | 0.01012% | 0.01012% | 0.008835% | 0.008835% | 0.006838% | 0.006838% | 0.001691% | 0.001691% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-12 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003813% | 0.003813% | 0.005423% | 0.005423% | 0.007301% | 0.007301% | 0.008183% | 0.008183% | 0.00561% | 0.00561% | 0.00638% | 0.00638% | 0.001776% | 0.001776% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-13 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002712% | 0.002712% | 0.006172% | 0.006172% | 0.006313% | 0.006313% | 0.007052% | 0.007052% | 0.01028% | 0.01028% | 0.004461% | 0.004461% | 0.001787% | 0.001787% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005784% | 0.005784% | 0.01073% | 0.01073% | 0.008146% | 0.008146% | 0.01323% | 0.01323% | 0.01095% | 0.01095% | 0.005029% | 0.005029% | 0.003401% | 0.003401% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-15 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004416% | 0.004416% | 0.007703% | 0.007703% | 0.009543% | 0.009543% | 0.00887% | 0.00887% | 0.006509% | 0.006509% | 0.006456% | 0.006456% | 0.001893% | 0.001893% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-16 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.008558% | 0.008558% | 0.01194% | 0.01194% | 0.01253% | 0.01253% | 0.00937% | 0.00937% | 0.004132% | 0.004132% | 0.004307% | 0.004307% | 0.001402% | 0.001402% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-17 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005394% | 0.005394% | 0.008831% | 0.008831% | 0.01234% | 0.01234% | 0.01299% | 0.01299% | 0.0107% | 0.0107% | 0.005711% | 0.005711% | 0.003061% | 0.003061% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-18 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002789% | 0.002789% | 0.007464% | 0.007464% | 0.008871% | 0.008871% | 0.007035% | 0.007035% | 0.007107% | 0.007107% | 0.005325% | 0.005325% | 0.001911% | 0.001911% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-19 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004844% | 0.004844% | 0.009926% | 0.009926% | 0.01742% | 0.01742% | 0.0141% | 0.0141% | 0.00773% | 0.00773% | 0.007245% | 0.007245% | 0.003392% | 0.003392% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-20 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.008213% | 0.008213% | 0.01455% | 0.01455% | 0.01307% | 0.01307% | 0.009692% | 0.009692% | 0.00944% | 0.00944% | 0.004781% | 0.004781% | 0.001815% | 0.001815% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-21 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002122% | 0.002122% | 0.006857% | 0.006857% | 0.005909% | 0.005909% | 0.006804% | 0.006804% | 0.003343% | 0.003343% | 0.003447% | 0.003447% | 0.001312% | 0.001312% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-22 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004717% | 0.004717% | 0.008638% | 0.008638% | 0.01034% | 0.01034% | 0.0117% | 0.0117% | 0.01008% | 0.01008% | 0.006383% | 0.006383% | 0.002149% | 0.002149% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004203% | 0.004203% | 0.005303% | 0.005303% | 0.006436% | 0.006436% | 0.006339% | 0.006339% | 0.004753% | 0.004753% | 0.006458% | 0.006458% | 0.001372% | 0.001372% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004104% | 0.004104% | 0.007208% | 0.007208% | 0.01001% | 0.01001% | 0.008955% | 0.008955% | 0.007553% | 0.007553% | 0.005822% | 0.005822% | 0.002185% | 0.002185% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-25 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002678% | 0.002678% | 0.003436% | 0.003436% | 0.004535% | 0.004535% | 0.005537% | 0.005537% | 0.00725% | 0.00725% | 0.005101% | 0.005101% | 0.001647% | 0.001647% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-26 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003178% | 0.003178% | 0.009399% | 0.009399% | 0.01025% | 0.01025% | 0.01081% | 0.01081% | 0.008282% | 0.008282% | 0.00689% | 0.00689% | 0.002103% | 0.002103% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-27 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004464% | 0.004464% | 0.007179% | 0.007179% | 0.01238% | 0.01238% | 0.01166% | 0.01166% | 0.01215% | 0.01215% | 0.01095% | 0.01095% | 0.002943% | 0.002943% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004177% | 0.004177% | 0.008385% | 0.008385% | 0.01239% | 0.01239% | 0.01609% | 0.01609% | 0.01773% | 0.01773% | 0.01217% | 0.01217% | 0.003427% | 0.003427% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-29 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003487% | 0.003487% | 0.007778% | 0.007778% | 0.01131% | 0.01131% | 0.01215% | 0.01215% | 0.01311% | 0.01311% | 0.007326% | 0.007326% | 0.003519% | 0.003519% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-30 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003088% | 0.003088% | 0.005734% | 0.005734% | 0.007272% | 0.007272% | 0.004909% | 0.004909% | 0.005071% | 0.005071% | 0.004968% | 0.004968% | 0.003153% | 0.003153% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2022-12-31 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003353% | 0.003353% | 0.007862% | 0.007862% | 0.006054% | 0.006054% | 0.005692% | 0.005692% | 0.005668% | 0.005668% | 0.005247% | 0.005247% | 0.002279% | 0.002279% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total by HH | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.004974% | 0.004974% | 0.1575% | 0.1575% | 0.7352% | 0.7352% | 2.131% | 2.131% | 3.96% | 3.96% | 5.506% | 5.506% | 6.289% | 6.289% | 6.55% | 6.55% | 6.352% | 6.352% | 5.851% | 5.851% | 4.768% | 4.768% | 3.581% | 3.581% | 2.342% | 2.342% | 1.24% | 1.24% | 0.4387% | 0.4387% | 0.09536% | 0.09536% | 0% | 0% | 0% | 0% | 0% | 0%
Year total | 100%

## Solar PV generation (hidden)
Date | 0:00 | 0:30 | 1:00 | 1:30 | 2:00 | 2:30 | 3:00 | 3:30 | 4:00 | 4:30 | 5:00 | 5:30 | 6:00 | 6:30 | 7:00 | 7:30 | 8:00 | 8:30 | 9:00 | 9:30 | 10:00 | 10:30 | 11:00 | 11:30 | 12:00 | 12:30 | 13:00 | 13:30 | 14:00 | 14:30 | 15:00 | 15:30 | 16:00 | 16:30 | 17:00 | 17:30 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 20:30 | 21:00 | 21:30 | 22:00 | 22:30 | 23:00 | 23:30
2022-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2282 | 2.2282 | 2.8816 | 2.8816 | 3.1253 | 3.1253 | 3.887 | 3.887 | 3.0746 | 3.0746 | 2.1762 | 2.1762 | 1.54 | 1.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8383 | 4.8383 | 9.4065 | 9.4065 | 10.8164 | 10.8164 | 11.4638 | 11.4638 | 10.5804 | 10.5804 | 7.0557 | 7.0557 | 2.942 | 2.942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.962 | 2.962 | 8.2614 | 8.2614 | 5.8757 | 5.8757 | 6.537 | 6.537 | 4.0651 | 4.0651 | 8.5616 | 8.5616 | 3.8987 | 3.8987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.132 | 5.132 | 8.9255 | 8.9255 | 10.295 | 10.295 | 6.5234 | 6.5234 | 9.5399 | 9.5399 | 8.9264 | 8.9264 | 4.0091 | 4.0091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8006 | 5.8006 | 9.3874 | 9.3874 | 16.6832 | 16.6832 | 15.137 | 15.137 | 9.8969 | 9.8969 | 8.2624 | 8.2624 | 3.0085 | 3.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9332 | 3.9332 | 6.0152 | 6.0152 | 13.8131 | 13.8131 | 14.6066 | 14.6066 | 10.1058 | 10.1058 | 8.6023 | 8.6023 | 2.6551 | 2.6551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3015 | 3.3015 | 8.9217 | 8.9217 | 6.5036 | 6.5036 | 7.6505 | 7.6505 | 7.2838 | 7.2838 | 8.5849 | 8.5849 | 4.4529 | 4.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4177 | 2.4177 | 6.3012 | 6.3012 | 6.0686 | 6.0686 | 8.1468 | 8.1468 | 8.2725 | 8.2725 | 5.1989 | 5.1989 | 4.9402 | 4.9402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6993 | 5.6993 | 13.5717 | 13.5717 | 12.1933 | 12.1933 | 10.2221 | 10.2221 | 9.2943 | 9.2943 | 6.8171 | 6.8171 | 1.7199 | 1.7199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3095 | 2.3095 | 4.7764 | 4.7764 | 10.8024 | 10.8024 | 13.283 | 13.283 | 17.8328 | 17.8328 | 8.0471 | 8.0471 | 3.2898 | 3.2898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0098 | 5.0098 | 10.2967 | 10.2967 | 8.8415 | 8.8415 | 12.6358 | 12.6358 | 11.2328 | 11.2328 | 3.498 | 3.498 | 3.0417 | 3.0417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1726 | 3.1726 | 7.2723 | 7.2723 | 5.7108 | 5.7108 | 4.5291 | 4.5291 | 2.4004 | 2.4004 | 5.2188 | 5.2188 | 4.6976 | 4.6976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3219 | 5.3219 | 7.3072 | 7.3072 | 13.4129 | 13.4129 | 12.8599 | 12.8599 | 6.3169 | 6.3169 | 5.0679 | 5.0679 | 3.0602 | 3.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8305 | 2.8305 | 6.9866 | 6.9866 | 7.7981 | 7.7981 | 7.7004 | 7.7004 | 8.091 | 8.091 | 6.5504 | 6.5504 | 3.3448 | 3.3448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8072 | 3.8072 | 5.7061 | 5.7061 | 9.2008 | 9.2008 | 17.335 | 17.335 | 15.4513 | 15.4513 | 8.5694 | 8.5694 | 7.9081 | 7.9081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7742 | 5.7742 | 10.4282 | 10.4282 | 13.6116 | 13.6116 | 11.041 | 11.041 | 13.4973 | 13.4973 | 13.2946 | 13.2946 | 7.3319 | 7.3319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2793 | 7.2793 | 14.1061 | 14.1061 | 15.1372 | 15.1372 | 17.3521 | 17.3521 | 15.356 | 15.356 | 12.2532 | 12.2532 | 7.743 | 7.743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9933 | 7.9933 | 15.7231 | 15.7231 | 20.11 | 20.11 | 16.5283 | 16.5283 | 15.7948 | 15.7948 | 12.0628 | 12.0628 | 7.9996 | 7.9996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2602 | 8.2602 | 20.6183 | 20.6183 | 24.1943 | 24.1943 | 25.0577 | 25.0577 | 24.224 | 24.224 | 18.2161 | 18.2161 | 11.329 | 11.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4774 | 6.4774 | 12.6819 | 12.6819 | 18.4947 | 18.4947 | 18.1642 | 18.1642 | 18.1544 | 18.1544 | 16.7352 | 16.7352 | 8.4973 | 8.4973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.648 | 5.648 | 10.6333 | 10.6333 | 12.4718 | 12.4718 | 13.4443 | 13.4443 | 16.1676 | 16.1676 | 12.3648 | 12.3648 | 8.3621 | 8.3621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5663 | 4.5663 | 11.6247 | 11.6247 | 12.5644 | 12.5644 | 15.0389 | 15.0389 | 12.0453 | 12.0453 | 11.4491 | 11.4491 | 5.0848 | 5.0848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4897 | 5.4897 | 10.9913 | 10.9913 | 12.8961 | 12.8961 | 8.6536 | 8.6536 | 8.3986 | 8.3986 | 7.9875 | 7.9875 | 4.8437 | 4.8437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6113 | 7.6113 | 9.9508 | 9.9508 | 12.6767 | 12.6767 | 15.0089 | 15.0089 | 14.0745 | 14.0745 | 8.9789 | 8.9789 | 5.9994 | 5.9994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5217 | 8.5217 | 11.0686 | 11.0686 | 11.1919 | 11.1919 | 9.2365 | 9.2365 | 8.8373 | 8.8373 | 6.104 | 6.104 | 3.4594 | 3.4594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2142 | 2.2142 | 3.3972 | 3.3972 | 5.731 | 5.731 | 11.2212 | 11.2212 | 9.0631 | 9.0631 | 4.9182 | 4.9182 | 2.6509 | 2.6509 | 0.32467 | 0.32467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42067 | 0.42067 | 5.211 | 5.211 | 13.1 | 13.1 | 11.5667 | 11.5667 | 10.5521 | 10.5521 | 4.4327 | 4.4327 | 2.8724 | 2.8724 | 2.2839 | 2.2839 | 0.19124 | 0.19124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54212 | 0.54212 | 6.4402 | 6.4402 | 12.536 | 12.536 | 19.9146 | 19.9146 | 19.1338 | 19.1338 | 15.355 | 15.355 | 9.3783 | 9.3783 | 11.0609 | 11.0609 | 0.84462 | 0.84462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4854 | 0.4854 | 6.426 | 6.426 | 11.9274 | 11.9274 | 13.1042 | 13.1042 | 13.768 | 13.768 | 8.5414 | 8.5414 | 9.9357 | 9.9357 | 5.2434 | 5.2434 | 0.77534 | 0.77534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59429 | 0.59429 | 6.6014 | 6.6014 | 10.1319 | 10.1319 | 14.2051 | 14.2051 | 14.7382 | 14.7382 | 13.5023 | 13.5023 | 8.835 | 8.835 | 4.2161 | 4.2161 | 1.4612 | 1.4612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-01-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37456 | 0.37456 | 3.0884 | 3.0884 | 3.7841 | 3.7841 | 4.0542 | 4.0542 | 6.1518 | 6.1518 | 4.7733 | 4.7733 | 5.3175 | 5.3175 | 4.5301 | 4.5301 | 0.59126 | 0.59126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71002 | 0.71002 | 8.6148 | 8.6148 | 9.5527 | 9.5527 | 10.2362 | 10.2362 | 7.6501 | 7.6501 | 3.9455 | 3.9455 | 10.446 | 10.446 | 6.3435 | 6.3435 | 1.4146 | 1.4146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3883 | 1.3883 | 5.5214 | 5.5214 | 8.2044 | 8.2044 | 12.7321 | 12.7321 | 13.0092 | 13.0092 | 11.7937 | 11.7937 | 10.574 | 10.574 | 8.5252 | 8.5252 | 1.8546 | 1.8546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7138 | 1.7138 | 5.5525 | 5.5525 | 9.9633 | 9.9633 | 9.2128 | 9.2128 | 11.2846 | 11.2846 | 9.6547 | 9.6547 | 6.2486 | 6.2486 | 5.9047 | 5.9047 | 1.9101 | 1.9101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1808 | 2.1808 | 5.3358 | 5.3358 | 7.6562 | 7.6562 | 11.0946 | 11.0946 | 10.5303 | 10.5303 | 10.7752 | 10.7752 | 5.8728 | 5.8728 | 6.4282 | 6.4282 | 2.7417 | 2.7417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4041 | 2.4041 | 4.7108 | 4.7108 | 7.0938 | 7.0938 | 9.6929 | 9.6929 | 11.6624 | 11.6624 | 9.9401 | 9.9401 | 6.3655 | 6.3655 | 5.9457 | 5.9457 | 3.261 | 3.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7242 | 2.7242 | 10.8227 | 10.8227 | 19.4987 | 19.4987 | 19.7315 | 19.7315 | 14.5839 | 14.5839 | 18.3038 | 18.3038 | 16.1915 | 16.1915 | 10.0654 | 10.0654 | 4.3382 | 4.3382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1607 | 4.1607 | 10.0763 | 10.0763 | 14.5718 | 14.5718 | 16.318 | 16.318 | 16.2909 | 16.2909 | 18.3249 | 18.3249 | 16.0408 | 16.0408 | 6.7325 | 6.7325 | 2.7303 | 2.7303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6421 | 2.6421 | 9.7091 | 9.7091 | 12.7692 | 12.7692 | 17.7889 | 17.7889 | 16.3632 | 16.3632 | 16.8568 | 16.8568 | 12.6539 | 12.6539 | 9.0158 | 9.0158 | 4.3839 | 4.3839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1286 | 1.1286 | 3.038 | 3.038 | 7.544 | 7.544 | 9.2131 | 9.2131 | 12.6651 | 12.6651 | 13.2261 | 13.2261 | 11.2935 | 11.2935 | 6.8133 | 6.8133 | 3.8349 | 3.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3657 | 3.3657 | 4.8953 | 4.8953 | 8.1666 | 8.1666 | 8.476 | 8.476 | 7.8185 | 7.8185 | 5.2778 | 5.2778 | 8.9279 | 8.9279 | 3.8097 | 3.8097 | 1.5142 | 1.5142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5068 | 5.5068 | 11.8012 | 11.8012 | 16.8723 | 16.8723 | 19.2424 | 19.2424 | 13.8155 | 13.8155 | 11.9219 | 11.9219 | 13.1119 | 13.1119 | 8.9275 | 8.9275 | 4.9477 | 4.9477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3624 | 5.3624 | 10.0559 | 10.0559 | 12.7638 | 12.7638 | 14.3503 | 14.3503 | 14.4103 | 14.4103 | 10.6575 | 10.6575 | 11.1318 | 11.1318 | 10.0029 | 10.0029 | 3.7799 | 3.7799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3927 | 3.3927 | 5.6215 | 5.6215 | 12.9624 | 12.9624 | 10.6317 | 10.6317 | 11.172 | 11.172 | 15.3733 | 15.3733 | 9.6802 | 9.6802 | 8.0737 | 8.0737 | 4.4903 | 4.4903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0871 | 7.0871 | 11.6178 | 11.6178 | 14.8244 | 14.8244 | 14.9294 | 14.9294 | 9.4989 | 9.4989 | 10.8167 | 10.8167 | 6.8613 | 6.8613 | 9.9639 | 9.9639 | 2.2201 | 2.2201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0862 | 3.0862 | 7.2912 | 7.2912 | 11.7952 | 11.7952 | 11.7422 | 11.7422 | 10.427 | 10.427 | 10.6475 | 10.6475 | 11.0856 | 11.0856 | 10.8679 | 10.8679 | 5.4533 | 5.4533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6661 | 5.6661 | 9.4789 | 9.4789 | 17.9633 | 17.9633 | 19.3912 | 19.3912 | 19.8267 | 19.8267 | 17.9449 | 17.9449 | 17.3747 | 17.3747 | 9.5169 | 9.5169 | 3.1374 | 3.1374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6625 | 6.6625 | 13.1613 | 13.1613 | 17.7573 | 17.7573 | 22.3478 | 22.3478 | 23.989 | 23.989 | 19.4473 | 19.4473 | 22.8618 | 22.8618 | 16.049 | 16.049 | 8.6823 | 8.6823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8659 | 5.8659 | 12.7606 | 12.7606 | 20.1601 | 20.1601 | 24.8671 | 24.8671 | 22.0626 | 22.0626 | 20.4018 | 20.4018 | 15.1149 | 15.1149 | 12.6802 | 12.6802 | 7.297 | 7.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3252 | 5.3252 | 10.9575 | 10.9575 | 11.0599 | 11.0599 | 12.108 | 12.108 | 8.9596 | 8.9596 | 10.1168 | 10.1168 | 8.7007 | 8.7007 | 5.1764 | 5.1764 | 2.3394 | 2.3394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2625 | 4.2625 | 7.0315 | 7.0315 | 7.4078 | 7.4078 | 14.3159 | 14.3159 | 10.5423 | 10.5423 | 6.0869 | 6.0869 | 5.7091 | 5.7091 | 3.608 | 3.608 | 2.3301 | 2.3301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3558 | 4.3558 | 10.2867 | 10.2867 | 11.834 | 11.834 | 9.941 | 9.941 | 3.7713 | 3.7713 | 10.3012 | 10.3012 | 7.6381 | 7.6381 | 6.2733 | 6.2733 | 3.3067 | 3.3067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4695 | 4.4695 | 5.835 | 5.835 | 8.0402 | 8.0402 | 11.8196 | 11.8196 | 10.2261 | 10.2261 | 12.1737 | 12.1737 | 10.4888 | 10.4888 | 8.2077 | 8.2077 | 5.8891 | 5.8891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2441 | 6.2441 | 11.1655 | 11.1655 | 10.0534 | 10.0534 | 12.6423 | 12.6423 | 7.2196 | 7.2196 | 7.0676 | 7.0676 | 15.3138 | 15.3138 | 9.7279 | 9.7279 | 4.7372 | 4.7372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5856 | 8.5856 | 17.7764 | 17.7764 | 22.4177 | 22.4177 | 24.0939 | 24.0939 | 18.2563 | 18.2563 | 20.8272 | 20.8272 | 14.1269 | 14.1269 | 14.4628 | 14.4628 | 8.764 | 8.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2178 | 8.2178 | 13.2594 | 13.2594 | 12.3609 | 12.3609 | 16.2521 | 16.2521 | 14.0689 | 14.0689 | 17.4005 | 17.4005 | 13.2149 | 13.2149 | 10.9418 | 10.9418 | 6.3042 | 6.3042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1499 | 5.1499 | 8.8868 | 8.8868 | 8.7498 | 8.7498 | 15.7646 | 15.7646 | 15.3827 | 15.3827 | 10.1442 | 10.1442 | 11.0045 | 11.0045 | 5.838 | 5.838 | 5.8367 | 5.8367 | 0.36976 | 0.36976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0659 | 9.0659 | 11.5815 | 11.5815 | 11.2048 | 11.2048 | 12.3593 | 12.3593 | 10.766 | 10.766 | 14.7334 | 14.7334 | 13.7174 | 13.7174 | 11.5861 | 11.5861 | 7.8372 | 7.8372 | 0.86577 | 0.86577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-02-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27393 | 0.27393 | 5.5705 | 5.5705 | 10.7903 | 10.7903 | 14.4964 | 14.4964 | 11.521 | 11.521 | 8.5933 | 8.5933 | 10.8829 | 10.8829 | 5.9059 | 5.9059 | 8.1118 | 8.1118 | 3.4888 | 3.4888 | 0.54246 | 0.54246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48497 | 0.48497 | 6.9789 | 6.9789 | 9.9164 | 9.9164 | 14.5682 | 14.5682 | 12.5594 | 12.5594 | 13.5872 | 13.5872 | 19.5833 | 19.5833 | 12.87 | 12.87 | 11.1361 | 11.1361 | 6.2861 | 6.2861 | 1.0287 | 1.0287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3192 | 1.3192 | 3.5322 | 3.5322 | 7.7256 | 7.7256 | 9.8486 | 9.8486 | 10.6115 | 10.6115 | 9.8183 | 9.8183 | 17.7775 | 17.7775 | 15.5937 | 15.5937 | 11.402 | 11.402 | 9.4393 | 9.4393 | 1.9581 | 1.9581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2124 | 1.2124 | 8.3283 | 8.3283 | 10.5283 | 10.5283 | 14.2084 | 14.2084 | 17.2865 | 17.2865 | 7.1071 | 7.1071 | 15.491 | 15.491 | 15.8595 | 15.8595 | 10.8 | 10.8 | 6.2364 | 6.2364 | 1.187 | 1.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5339 | 1.5339 | 10.8359 | 10.8359 | 16.5664 | 16.5664 | 18.7345 | 18.7345 | 20.6489 | 20.6489 | 12.1236 | 12.1236 | 13.4879 | 13.4879 | 9.6205 | 9.6205 | 11.1607 | 11.1607 | 4.6345 | 4.6345 | 0.7321 | 0.7321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2086 | 1.2086 | 6.4685 | 6.4685 | 11.7476 | 11.7476 | 16.214 | 16.214 | 14.2963 | 14.2963 | 16.4683 | 16.4683 | 14.6426 | 14.6426 | 11.8341 | 11.8341 | 7.0002 | 7.0002 | 3.5654 | 3.5654 | 1.1743 | 1.1743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9906 | 1.9906 | 9.6549 | 9.6549 | 17.5478 | 17.5478 | 20.0764 | 20.0764 | 24.6193 | 24.6193 | 20.7068 | 20.7068 | 19.9919 | 19.9919 | 17.2641 | 17.2641 | 14.3691 | 14.3691 | 9.1172 | 9.1172 | 1.9643 | 1.9643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6661 | 1.6661 | 7.6931 | 7.6931 | 13.7583 | 13.7583 | 16.8104 | 16.8104 | 24.7505 | 24.7505 | 21.8534 | 21.8534 | 22.4722 | 22.4722 | 18.9816 | 18.9816 | 14.3373 | 14.3373 | 9.6661 | 9.6661 | 2.9624 | 2.9624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5978 | 1.5978 | 9.6937 | 9.6937 | 13.5941 | 13.5941 | 17.5881 | 17.5881 | 16.1201 | 16.1201 | 14.5791 | 14.5791 | 12.5886 | 12.5886 | 11.642 | 11.642 | 10.2677 | 10.2677 | 7.8387 | 7.8387 | 2.5513 | 2.5513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3649 | 2.3649 | 9.5824 | 9.5824 | 12.9971 | 12.9971 | 8.6664 | 8.6664 | 11.765 | 11.765 | 13.3346 | 13.3346 | 17.5961 | 17.5961 | 10.4501 | 10.4501 | 9.9708 | 9.9708 | 4.5998 | 4.5998 | 1.6446 | 1.6446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5211 | 1.5211 | 4.358 | 4.358 | 7.6032 | 7.6032 | 11.2964 | 11.2964 | 12.2682 | 12.2682 | 14.2046 | 14.2046 | 11.4739 | 11.4739 | 10.6691 | 10.6691 | 8.3487 | 8.3487 | 5.9932 | 5.9932 | 2.2436 | 2.2436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5006 | 2.5006 | 8.4179 | 8.4179 | 14.5496 | 14.5496 | 23.1703 | 23.1703 | 26.6623 | 26.6623 | 24.5975 | 24.5975 | 24.133 | 24.133 | 15.6855 | 15.6855 | 16.9268 | 16.9268 | 10.8026 | 10.8026 | 2.6683 | 2.6683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7361 | 2.7361 | 7.8658 | 7.8658 | 12.9356 | 12.9356 | 12.1404 | 12.1404 | 21.9996 | 21.9996 | 23.544 | 23.544 | 22.2902 | 22.2902 | 14.858 | 14.858 | 11.9872 | 11.9872 | 6.0334 | 6.0334 | 2.6224 | 2.6224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.578 | 3.578 | 10.7186 | 10.7186 | 10.9911 | 10.9911 | 18.5315 | 18.5315 | 20.5346 | 20.5346 | 21.3289 | 21.3289 | 24.6805 | 24.6805 | 22.5428 | 22.5428 | 18.621 | 18.621 | 12.2522 | 12.2522 | 3.8006 | 3.8006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6944 | 2.6944 | 8.3394 | 8.3394 | 14.849 | 14.849 | 21.6266 | 21.6266 | 18.0087 | 18.0087 | 17.7045 | 17.7045 | 22.2984 | 22.2984 | 19.7513 | 19.7513 | 14.7817 | 14.7817 | 9.3205 | 9.3205 | 2.8676 | 2.8676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8929 | 1.8929 | 5.2451 | 5.2451 | 8.0872 | 8.0872 | 10.6001 | 10.6001 | 13.9076 | 13.9076 | 13.8432 | 13.8432 | 10.7874 | 10.7874 | 10.4267 | 10.4267 | 9.8156 | 9.8156 | 6.4593 | 6.4593 | 3.2847 | 3.2847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.379 | 4.379 | 11.0664 | 11.0664 | 18.0262 | 18.0262 | 21.0429 | 21.0429 | 25.5436 | 25.5436 | 17.713 | 17.713 | 21.437 | 21.437 | 21.7153 | 21.7153 | 16.5799 | 16.5799 | 12.1364 | 12.1364 | 3.7649 | 3.7649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6704 | 3.6704 | 10.5532 | 10.5532 | 15.8735 | 15.8735 | 20.7045 | 20.7045 | 20.9197 | 20.9197 | 19.758 | 19.758 | 18.9251 | 18.9251 | 16.2822 | 16.2822 | 12.2123 | 12.2123 | 7.5136 | 7.5136 | 2.6015 | 2.6015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7967 | 2.7967 | 5.6669 | 5.6669 | 6.9516 | 6.9516 | 10.4716 | 10.4716 | 14.7504 | 14.7504 | 12.2356 | 12.2356 | 14.0878 | 14.0878 | 10.8069 | 10.8069 | 10.7971 | 10.7971 | 6.1415 | 6.1415 | 3.0595 | 3.0595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9503 | 1.9503 | 3.9347 | 3.9347 | 4.684 | 4.684 | 5.0021 | 5.0021 | 4.3614 | 4.3614 | 4.8016 | 4.8016 | 9.8109 | 9.8109 | 11.4627 | 11.4627 | 8.3264 | 8.3264 | 6.773 | 6.773 | 3.2015 | 3.2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9293 | 2.9293 | 5.6063 | 5.6063 | 11.557 | 11.557 | 11.0329 | 11.0329 | 10.4913 | 10.4913 | 15.0825 | 15.0825 | 14.9596 | 14.9596 | 14.4571 | 14.4571 | 12.3492 | 12.3492 | 8.7587 | 8.7587 | 4.8977 | 4.8977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1845 | 6.1845 | 11.9502 | 11.9502 | 17.9415 | 17.9415 | 25.4683 | 25.4683 | 27.0339 | 27.0339 | 23.6019 | 23.6019 | 21.0247 | 21.0247 | 21.1903 | 21.1903 | 13.5366 | 13.5366 | 10.1326 | 10.1326 | 4.2014 | 4.2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6733 | 4.6733 | 12.9556 | 12.9556 | 22.7994 | 22.7994 | 24.2645 | 24.2645 | 23.884 | 23.884 | 20.7574 | 20.7574 | 21.1262 | 21.1262 | 21.9507 | 21.9507 | 16.6753 | 16.6753 | 10.5824 | 10.5824 | 3.8935 | 3.8935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.572 | 4.572 | 9.5473 | 9.5473 | 18.7589 | 18.7589 | 23.6459 | 23.6459 | 25.594 | 25.594 | 25.2141 | 25.2141 | 20.6599 | 20.6599 | 19.8342 | 19.8342 | 14.4429 | 14.4429 | 10.4029 | 10.4029 | 4.8748 | 4.8748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1507 | 4.1507 | 7.4785 | 7.4785 | 12.3369 | 12.3369 | 17.1629 | 17.1629 | 16.2826 | 16.2826 | 12.4761 | 12.4761 | 14.7507 | 14.7507 | 16.2614 | 16.2614 | 17.831 | 17.831 | 10.5702 | 10.5702 | 3.8325 | 3.8325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6893 | 6.6893 | 15.3274 | 15.3274 | 23.8754 | 23.8754 | 25.4254 | 25.4254 | 28.8367 | 28.8367 | 24.7872 | 24.7872 | 29.4902 | 29.4902 | 23.9068 | 23.9068 | 21.1633 | 21.1633 | 16.0173 | 16.0173 | 7.6927 | 7.6927 | 0.2392 | 0.2392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.071811 | 0.071811 | 3.0769 | 3.0769 | 8.7392 | 8.7392 | 14.0324 | 14.0324 | 20.9628 | 20.9628 | 27.0391 | 27.0391 | 28.2852 | 28.2852 | 20.291 | 20.291 | 18.0992 | 18.0992 | 18.0886 | 18.0886 | 12.1653 | 12.1653 | 7.182 | 7.182 | 2.4956 | 2.4956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15947 | 0.15947 | 3.5138 | 3.5138 | 8.4948 | 8.4948 | 14.0186 | 14.0186 | 23.214 | 23.214 | 25.0025 | 25.0025 | 30.9091 | 30.9091 | 30.1079 | 30.1079 | 23.3979 | 23.3979 | 23.4037 | 23.4037 | 18.9552 | 18.9552 | 10.4963 | 10.4963 | 2.2653 | 2.2653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15947 | 0.15947 | 2.3003 | 2.3003 | 6.5939 | 6.5939 | 11.2922 | 11.2922 | 17.8654 | 17.8654 | 28.1664 | 28.1664 | 20.7638 | 20.7638 | 16.6822 | 16.6822 | 13.7742 | 13.7742 | 15.0759 | 15.0759 | 15.6213 | 15.6213 | 7.1838 | 7.1838 | 1.48 | 1.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54473 | 0.54473 | 6.696 | 6.696 | 13.154 | 13.154 | 16.3212 | 16.3212 | 10.1165 | 10.1165 | 16.5559 | 16.5559 | 13.7351 | 13.7351 | 15.2595 | 15.2595 | 12.8844 | 12.8844 | 9.625 | 9.625 | 4.3858 | 4.3858 | 3.4178 | 3.4178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59606 | 0.59606 | 6.6129 | 6.6129 | 9.4612 | 9.4612 | 18.0718 | 18.0718 | 20.8354 | 20.8354 | 21.4496 | 21.4496 | 17.425 | 17.425 | 16.1488 | 16.1488 | 13.6127 | 13.6127 | 12.4826 | 12.4826 | 7.2123 | 7.2123 | 3.3022 | 3.3022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-03-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57078 | 0.57078 | 5.7475 | 5.7475 | 14.0829 | 14.0829 | 17.1972 | 17.1972 | 18.2612 | 18.2612 | 18.436 | 18.436 | 19.1026 | 19.1026 | 17.2284 | 17.2284 | 16.3338 | 16.3338 | 11.1859 | 11.1859 | 12.3455 | 12.3455 | 6.3466 | 6.3466 | 0.16486 | 0.16486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0115 | 1.0115 | 7.4887 | 7.4887 | 15.8636 | 15.8636 | 23.4188 | 23.4188 | 19.8486 | 19.8486 | 16.6163 | 16.6163 | 13.4069 | 13.4069 | 15.2396 | 15.2396 | 11.9548 | 11.9548 | 10.7156 | 10.7156 | 7.2185 | 7.2185 | 4.0256 | 4.0256 | 0.27747 | 0.27747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83198 | 0.83198 | 4.9178 | 4.9178 | 12.3487 | 12.3487 | 19.8205 | 19.8205 | 18.5862 | 18.5862 | 20.008 | 20.008 | 24.997 | 24.997 | 20.7441 | 20.7441 | 16.5932 | 16.5932 | 13.5889 | 13.5889 | 7.2438 | 7.2438 | 2.92 | 2.92 | 0.2912 | 0.2912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92342 | 0.92342 | 5.14 | 5.14 | 12.5254 | 12.5254 | 14.6517 | 14.6517 | 17.2199 | 17.2199 | 18.4352 | 18.4352 | 20.933 | 20.933 | 19.4706 | 19.4706 | 16.3041 | 16.3041 | 15.2387 | 15.2387 | 9.9224 | 9.9224 | 3.6645 | 3.6645 | 0.33857 | 0.33857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1622 | 1.1622 | 5.2788 | 5.2788 | 9.7924 | 9.7924 | 15.8524 | 15.8524 | 14.7187 | 14.7187 | 16.8533 | 16.8533 | 16.2217 | 16.2217 | 13.684 | 13.684 | 11.7054 | 11.7054 | 13.5318 | 13.5318 | 8.0183 | 8.0183 | 5.3031 | 5.3031 | 0.46138 | 0.46138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5309 | 1.5309 | 9.4617 | 9.4617 | 18.5754 | 18.5754 | 24.9148 | 24.9148 | 27.9987 | 27.9987 | 32.2307 | 32.2307 | 29.7278 | 29.7278 | 34.2787 | 34.2787 | 27.8181 | 27.8181 | 24.8678 | 24.8678 | 15.8257 | 15.8257 | 6.8822 | 6.8822 | 0.62885 | 0.62885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4371 | 1.4371 | 6.2788 | 6.2788 | 11.189 | 11.189 | 17.0347 | 17.0347 | 24.5174 | 24.5174 | 31.867 | 31.867 | 34.7286 | 34.7286 | 28.2683 | 28.2683 | 26.3823 | 26.3823 | 19.6437 | 19.6437 | 13.9287 | 13.9287 | 6.2148 | 6.2148 | 0.67832 | 0.67832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9895 | 1.9895 | 8.4908 | 8.4908 | 15.7603 | 15.7603 | 21.4282 | 21.4282 | 27.5993 | 27.5993 | 28.1022 | 28.1022 | 27.7716 | 27.7716 | 26.9992 | 26.9992 | 23.5038 | 23.5038 | 21.7066 | 21.7066 | 12.707 | 12.707 | 5.5755 | 5.5755 | 0.63905 | 0.63905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1869 | 2.1869 | 7.8297 | 7.8297 | 13.6202 | 13.6202 | 19.1198 | 19.1198 | 24.329 | 24.329 | 26.4515 | 26.4515 | 19.6202 | 19.6202 | 20.1372 | 20.1372 | 18.1881 | 18.1881 | 16.5351 | 16.5351 | 11.0412 | 11.0412 | 5.2144 | 5.2144 | 0.74263 | 0.74263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9941 | 1.9941 | 7.1297 | 7.1297 | 12.913 | 12.913 | 21.5917 | 21.5917 | 28.4301 | 28.4301 | 30.1248 | 30.1248 | 30.0722 | 30.0722 | 29.6513 | 29.6513 | 21.7949 | 21.7949 | 18.3323 | 18.3323 | 12.2084 | 12.2084 | 6.1394 | 6.1394 | 0.71288 | 0.71288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2854 | 2.2854 | 9.7401 | 9.7401 | 15.8188 | 15.8188 | 24.6477 | 24.6477 | 24.9345 | 24.9345 | 27.6705 | 27.6705 | 27.2295 | 27.2295 | 24.268 | 24.268 | 21.6142 | 21.6142 | 17.2123 | 17.2123 | 10.7071 | 10.7071 | 5.9524 | 5.9524 | 0.96675 | 0.96675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0026 | 2.0026 | 6.6421 | 6.6421 | 13.4733 | 13.4733 | 17.0974 | 17.0974 | 23.5797 | 23.5797 | 30.523 | 30.523 | 26.7496 | 26.7496 | 22.4866 | 22.4866 | 13.9442 | 13.9442 | 12.9459 | 12.9459 | 10.6253 | 10.6253 | 6.0774 | 6.0774 | 1.0055 | 1.0055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6251 | 2.6251 | 6.8158 | 6.8158 | 14.1265 | 14.1265 | 21.1965 | 21.1965 | 25.4118 | 25.4118 | 26.9258 | 26.9258 | 30.1591 | 30.1591 | 23.6858 | 23.6858 | 22.9908 | 22.9908 | 22.3334 | 22.3334 | 14.3744 | 14.3744 | 6.1777 | 6.1777 | 0.9053 | 0.9053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2818 | 2.2818 | 7.4387 | 7.4387 | 11.2138 | 11.2138 | 15.2212 | 15.2212 | 19.9649 | 19.9649 | 18.2658 | 18.2658 | 22.2155 | 22.2155 | 24.0089 | 24.0089 | 18.8537 | 18.8537 | 16.1727 | 16.1727 | 10.901 | 10.901 | 5.6438 | 5.6438 | 1.182 | 1.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9916 | 2.9916 | 10.4553 | 10.4553 | 16.5211 | 16.5211 | 25.103 | 25.103 | 28.9974 | 28.9974 | 34.1964 | 34.1964 | 35.2279 | 35.2279 | 30.1283 | 30.1283 | 22.9288 | 22.9288 | 20.8011 | 20.8011 | 14.3123 | 14.3123 | 6.9178 | 6.9178 | 0.97636 | 0.97636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4692 | 2.4692 | 8.8027 | 8.8027 | 14.0194 | 14.0194 | 19.2393 | 19.2393 | 22.8593 | 22.8593 | 27.3066 | 27.3066 | 30.1425 | 30.1425 | 28.9861 | 28.9861 | 22.1648 | 22.1648 | 18.0904 | 18.0904 | 13.3318 | 13.3318 | 7.0833 | 7.0833 | 1.5023 | 1.5023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1206 | 3.1206 | 8.4847 | 8.4847 | 17.0968 | 17.0968 | 25.6362 | 25.6362 | 23.7247 | 23.7247 | 23.0001 | 23.0001 | 20.9788 | 20.9788 | 16.9836 | 16.9836 | 12.7547 | 12.7547 | 13.0009 | 13.0009 | 8.8601 | 8.8601 | 5.9386 | 5.9386 | 1.5597 | 1.5597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4467 | 3.4467 | 9.8081 | 9.8081 | 15.9303 | 15.9303 | 22.1138 | 22.1138 | 25.9682 | 25.9682 | 26.0431 | 26.0431 | 25.272 | 25.272 | 22.2586 | 22.2586 | 21.2114 | 21.2114 | 16.1368 | 16.1368 | 10.8714 | 10.8714 | 5.5399 | 5.5399 | 1.286 | 1.286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.88 | 3.88 | 10.021 | 10.021 | 18.1331 | 18.1331 | 24.0047 | 24.0047 | 21.4601 | 21.4601 | 26.5565 | 26.5565 | 27.5324 | 27.5324 | 27.2321 | 27.2321 | 24.3038 | 24.3038 | 20.0854 | 20.0854 | 13.8117 | 13.8117 | 6.9092 | 6.9092 | 1.6095 | 1.6095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6542 | 3.6542 | 10.9425 | 10.9425 | 18.8286 | 18.8286 | 24.6514 | 24.6514 | 30.65 | 30.65 | 37.2939 | 37.2939 | 36.1974 | 36.1974 | 34.7358 | 34.7358 | 30.623 | 30.623 | 24.1705 | 24.1705 | 19.0411 | 19.0411 | 9.1522 | 9.1522 | 1.6896 | 1.6896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1512 | 4.1512 | 13.0759 | 13.0759 | 22.7957 | 22.7957 | 31.1808 | 31.1808 | 35.2997 | 35.2997 | 38.9118 | 38.9118 | 39.9486 | 39.9486 | 37.1756 | 37.1756 | 30.3613 | 30.3613 | 26.1523 | 26.1523 | 17.8332 | 17.8332 | 9.2105 | 9.2105 | 1.8308 | 1.8308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4104 | 3.4104 | 9.6267 | 9.6267 | 16.8058 | 16.8058 | 24.5698 | 24.5698 | 30.4638 | 30.4638 | 37.4106 | 37.4106 | 33.4884 | 33.4884 | 32.639 | 32.639 | 26.2756 | 26.2756 | 19.2599 | 19.2599 | 11.0574 | 11.0574 | 7.0378 | 7.0378 | 1.5964 | 1.5964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0409 | 4.0409 | 9.9101 | 9.9101 | 16.3105 | 16.3105 | 21.721 | 21.721 | 25.5698 | 25.5698 | 29.1538 | 29.1538 | 30.5961 | 30.5961 | 29.3708 | 29.3708 | 26.1207 | 26.1207 | 14.337 | 14.337 | 13.2083 | 13.2083 | 6.022 | 6.022 | 1.4877 | 1.4877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14497 | 0.14497 | 4.0683 | 4.0683 | 10.4544 | 10.4544 | 14.8448 | 14.8448 | 18.5995 | 18.5995 | 21.2588 | 21.2588 | 22.828 | 22.828 | 26.5678 | 26.5678 | 27.7327 | 27.7327 | 24.0146 | 24.0146 | 21.7376 | 21.7376 | 15.9649 | 15.9649 | 8.0398 | 8.0398 | 2.142 | 2.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28994 | 0.28994 | 3.9187 | 3.9187 | 8.8843 | 8.8843 | 17.0848 | 17.0848 | 17.9753 | 17.9753 | 22.0921 | 22.0921 | 29.2188 | 29.2188 | 24.2786 | 24.2786 | 23.3097 | 23.3097 | 16.3009 | 16.3009 | 15.0023 | 15.0023 | 9.1186 | 9.1186 | 4.5102 | 4.5102 | 1.6618 | 1.6618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21366 | 0.21366 | 3.3441 | 3.3441 | 7.7675 | 7.7675 | 13.0214 | 13.0214 | 16.1216 | 16.1216 | 22.6896 | 22.6896 | 23.8045 | 23.8045 | 15.2768 | 15.2768 | 18.5857 | 18.5857 | 23.0195 | 23.0195 | 20.764 | 20.764 | 14.9342 | 14.9342 | 6.0531 | 6.0531 | 1.743 | 1.743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43483 | 0.43483 | 4.5473 | 4.5473 | 11.1354 | 11.1354 | 15.1653 | 15.1653 | 21.0071 | 21.0071 | 22.6383 | 22.6383 | 23.8319 | 23.8319 | 23.3574 | 23.3574 | 18.8749 | 18.8749 | 19.0482 | 19.0482 | 16.8085 | 16.8085 | 13.858 | 13.858 | 7.5856 | 7.5856 | 2.1268 | 2.1268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49585 | 0.49585 | 4.1963 | 4.1963 | 10.5726 | 10.5726 | 17.9583 | 17.9583 | 21.5258 | 21.5258 | 18.2214 | 18.2214 | 24.5153 | 24.5153 | 12.1746 | 12.1746 | 15.8551 | 15.8551 | 14.5455 | 14.5455 | 11.8815 | 11.8815 | 12.2087 | 12.2087 | 5.8722 | 5.8722 | 1.4616 | 1.4616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51886 | 0.51886 | 4.372 | 4.372 | 8.7044 | 8.7044 | 9.9806 | 9.9806 | 16.28 | 16.28 | 18.1682 | 18.1682 | 21.096 | 21.096 | 10.3574 | 10.3574 | 16.6382 | 16.6382 | 15.5587 | 15.5587 | 12.5961 | 12.5961 | 8.0276 | 8.0276 | 4.4404 | 4.4404 | 2.0036 | 2.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54928 | 0.54928 | 3.3046 | 3.3046 | 8.309 | 8.309 | 14.0709 | 14.0709 | 18.1997 | 18.1997 | 12.1031 | 12.1031 | 12.9697 | 12.9697 | 14.236 | 14.236 | 12.2569 | 12.2569 | 13.1847 | 13.1847 | 15.243 | 15.243 | 11.3913 | 11.3913 | 7.2677 | 7.2677 | 2.0441 | 2.0441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-04-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64082 | 0.64082 | 4.5739 | 4.5739 | 10.8086 | 10.8086 | 15.8814 | 15.8814 | 17.8701 | 17.8701 | 21.8514 | 21.8514 | 23.0049 | 23.0049 | 22.0025 | 22.0025 | 16.1194 | 16.1194 | 10.6675 | 10.6675 | 11.5851 | 11.5851 | 9.4214 | 9.4214 | 7.3152 | 7.3152 | 2.2568 | 2.2568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87724 | 0.87724 | 4.4373 | 4.4373 | 11.5099 | 11.5099 | 19.3763 | 19.3763 | 22.1 | 22.1 | 22.8609 | 22.8609 | 26.8765 | 26.8765 | 26.3726 | 26.3726 | 32.4319 | 32.4319 | 25.6863 | 25.6863 | 17.0936 | 17.0936 | 11.0547 | 11.0547 | 6.5448 | 6.5448 | 2.4218 | 2.4218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74761 | 0.74761 | 3.5753 | 3.5753 | 6.7393 | 6.7393 | 12.2083 | 12.2083 | 16.7742 | 16.7742 | 22.434 | 22.434 | 21.522 | 21.522 | 20.9368 | 20.9368 | 21.2833 | 21.2833 | 12.0847 | 12.0847 | 11.9211 | 11.9211 | 6.455 | 6.455 | 4.8069 | 4.8069 | 2.0683 | 2.0683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90783 | 0.90783 | 4.0808 | 4.0808 | 5.6047 | 5.6047 | 10.7692 | 10.7692 | 16.406 | 16.406 | 20.1309 | 20.1309 | 21.8663 | 21.8663 | 17.5264 | 17.5264 | 15.6997 | 15.6997 | 19.7798 | 19.7798 | 17.9862 | 17.9862 | 11.3701 | 11.3701 | 7.1848 | 7.1848 | 2.385 | 2.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82388 | 0.82388 | 4.3631 | 4.3631 | 7.4764 | 7.4764 | 19.5123 | 19.5123 | 25.4993 | 25.4993 | 28.2492 | 28.2492 | 32.1764 | 32.1764 | 30.869 | 30.869 | 29.6776 | 29.6776 | 19.5313 | 19.5313 | 17.9263 | 17.9263 | 13.4818 | 13.4818 | 7.6627 | 7.6627 | 2.2258 | 2.2258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0986 | 1.0986 | 5.813 | 5.813 | 11.6461 | 11.6461 | 20.3564 | 20.3564 | 24.9383 | 24.9383 | 26.5871 | 26.5871 | 34.2611 | 34.2611 | 36.6776 | 36.6776 | 36.3555 | 36.3555 | 31.8028 | 31.8028 | 24.103 | 24.103 | 15.0074 | 15.0074 | 8.3696 | 8.3696 | 2.4476 | 2.4476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2358 | 1.2358 | 5.5347 | 5.5347 | 13.7528 | 13.7528 | 21.4378 | 21.4378 | 27.3369 | 27.3369 | 30.5786 | 30.5786 | 30.5402 | 30.5402 | 33.736 | 33.736 | 29.686 | 29.686 | 30.5627 | 30.5627 | 25.2282 | 25.2282 | 16.8711 | 16.8711 | 7.6084 | 7.6084 | 2.336 | 2.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2587 | 1.2587 | 5.1538 | 5.1538 | 11.9207 | 11.9207 | 16.392 | 16.392 | 25.2162 | 25.2162 | 30.1279 | 30.1279 | 30.4203 | 30.4203 | 31.7808 | 31.7808 | 28.6576 | 28.6576 | 26.8501 | 26.8501 | 22.4209 | 22.4209 | 16.9883 | 16.9883 | 9.9515 | 9.9515 | 2.7917 | 2.7917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2281 | 1.2281 | 4.8668 | 4.8668 | 10.1765 | 10.1765 | 17.6128 | 17.6128 | 21.9559 | 21.9559 | 24.0261 | 24.0261 | 29.4945 | 29.4945 | 31.0821 | 31.0821 | 24.3153 | 24.3153 | 20.5885 | 20.5885 | 18.0667 | 18.0667 | 11.7422 | 11.7422 | 8.6286 | 8.6286 | 2.7805 | 2.7805 | 0.01534 | 0.01534 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.129 | 1.129 | 5.7366 | 5.7366 | 10.9205 | 10.9205 | 18.369 | 18.369 | 21.9672 | 21.9672 | 28.1738 | 28.1738 | 31.6486 | 31.6486 | 31.2335 | 31.2335 | 32.1517 | 32.1517 | 28.9242 | 28.9242 | 21.9532 | 21.9532 | 13.2781 | 13.2781 | 6.6064 | 6.6064 | 2.1692 | 2.1692 | 0.21366 | 0.21366 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0146 | 1.0146 | 4.5385 | 4.5385 | 10.8123 | 10.8123 | 15.7515 | 15.7515 | 23.4284 | 23.4284 | 28.3482 | 28.3482 | 28.3223 | 28.3223 | 26.8581 | 26.8581 | 23.0761 | 23.0761 | 20.3838 | 20.3838 | 17.265 | 17.265 | 12.5226 | 12.5226 | 6.4562 | 6.4562 | 2.7314 | 2.7314 | 0.32804 | 0.32804 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95351 | 0.95351 | 4.4105 | 4.4105 | 8.9396 | 8.9396 | 15.8714 | 15.8714 | 22.016 | 22.016 | 24.5373 | 24.5373 | 27.3887 | 27.3887 | 23.5102 | 23.5102 | 15.1656 | 15.1656 | 18.6355 | 18.6355 | 16.1239 | 16.1239 | 13.8703 | 13.8703 | 8.3518 | 8.3518 | 3.1137 | 3.1137 | 0.16031 | 0.16031 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2282 | 1.2282 | 5.101 | 5.101 | 9.5597 | 9.5597 | 13.9298 | 13.9298 | 21.2303 | 21.2303 | 26.1012 | 26.1012 | 25.9951 | 25.9951 | 21.9447 | 21.9447 | 24.8004 | 24.8004 | 23.5141 | 23.5141 | 23.2028 | 23.2028 | 15.0918 | 15.0918 | 8.4146 | 8.4146 | 2.6572 | 2.6572 | 0.39664 | 0.39664 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4417 | 1.4417 | 4.6825 | 4.6825 | 10.5324 | 10.5324 | 16.2816 | 16.2816 | 23.8031 | 23.8031 | 23.5577 | 23.5577 | 26.6567 | 26.6567 | 27.1519 | 27.1519 | 27.3471 | 27.3471 | 22.9275 | 22.9275 | 20.5542 | 20.5542 | 14.1811 | 14.1811 | 7.5629 | 7.5629 | 3.461 | 3.461 | 0.51119 | 0.51119 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2053 | 1.2053 | 4.3915 | 4.3915 | 11.0526 | 11.0526 | 15.2524 | 15.2524 | 20.0578 | 20.0578 | 25.2742 | 25.2742 | 27.0078 | 27.0078 | 28.5504 | 28.5504 | 20.3869 | 20.3869 | 17.5162 | 17.5162 | 17.8506 | 17.8506 | 14.3437 | 14.3437 | 8.7415 | 8.7415 | 2.8841 | 2.8841 | 0.48068 | 0.48068 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3427 | 1.3427 | 5.1613 | 5.1613 | 12.6826 | 12.6826 | 21.3675 | 21.3675 | 27.407 | 27.407 | 27.5277 | 27.5277 | 29.1969 | 29.1969 | 31.0309 | 31.0309 | 27.2964 | 27.2964 | 27.5343 | 27.5343 | 22.649 | 22.649 | 14.9212 | 14.9212 | 8.4329 | 8.4329 | 2.7377 | 2.7377 | 0.61798 | 0.61798 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.663 | 1.663 | 4.5276 | 4.5276 | 6.9521 | 6.9521 | 13.3592 | 13.3592 | 20.0394 | 20.0394 | 25.1626 | 25.1626 | 22.8134 | 22.8134 | 28.0861 | 28.0861 | 28.4152 | 28.4152 | 23.0341 | 23.0341 | 18.1559 | 18.1559 | 16.1652 | 16.1652 | 8.1034 | 8.1034 | 3.5321 | 3.5321 | 0.52644 | 0.52644 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6401 | 1.6401 | 6.1802 | 6.1802 | 12.0232 | 12.0232 | 17.706 | 17.706 | 22.3415 | 22.3415 | 28.412 | 28.412 | 29.2388 | 29.2388 | 32.0474 | 32.0474 | 28.4513 | 28.4513 | 21.4426 | 21.4426 | 18.1792 | 18.1792 | 11.8236 | 11.8236 | 7.607 | 7.607 | 3.102 | 3.102 | 0.51886 | 0.51886 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4342 | 1.4342 | 4.7674 | 4.7674 | 10.6928 | 10.6928 | 16.5508 | 16.5508 | 21.9722 | 21.9722 | 23.6298 | 23.6298 | 24.0588 | 24.0588 | 23.4716 | 23.4716 | 22.1593 | 22.1593 | 19.5727 | 19.5727 | 16.4117 | 16.4117 | 14.683 | 14.683 | 9.1377 | 9.1377 | 3.0766 | 3.0766 | 0.46542 | 0.46542 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8384 | 1.8384 | 6.6919 | 6.6919 | 12.1461 | 12.1461 | 18.341 | 18.341 | 21.8715 | 21.8715 | 26.3609 | 26.3609 | 30.4264 | 30.4264 | 34.4395 | 34.4395 | 28.4219 | 28.4219 | 21.5928 | 21.5928 | 20.765 | 20.765 | 16.1836 | 16.1836 | 8.8159 | 8.8159 | 3.2768 | 3.2768 | 0.75528 | 0.75528 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8918 | 1.8918 | 7.1011 | 7.1011 | 15.0353 | 15.0353 | 20.8195 | 20.8195 | 23.9539 | 23.9539 | 23.9191 | 23.9191 | 33.473 | 33.473 | 36.278 | 36.278 | 32.7068 | 32.7068 | 23.814 | 23.814 | 22.0787 | 22.0787 | 17.2287 | 17.2287 | 10.9198 | 10.9198 | 3.8427 | 3.8427 | 0.8544 | 0.8544 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8613 | 1.8613 | 5.418 | 5.418 | 13.4345 | 13.4345 | 19.838 | 19.838 | 27.3278 | 27.3278 | 28.0955 | 28.0955 | 28.0272 | 28.0272 | 27.398 | 27.398 | 25.6857 | 25.6857 | 24.6881 | 24.6881 | 24.1219 | 24.1219 | 17.9808 | 17.9808 | 8.6268 | 8.6268 | 3.8576 | 3.8576 | 1.0223 | 1.0223 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8765 | 1.8765 | 4.9018 | 4.9018 | 11.6332 | 11.6332 | 20.2471 | 20.2471 | 28.3874 | 28.3874 | 28.3779 | 28.3779 | 38.5658 | 38.5658 | 33.555 | 33.555 | 28.6498 | 28.6498 | 25.5399 | 25.5399 | 20.6965 | 20.6965 | 15.4892 | 15.4892 | 9.7319 | 9.7319 | 3.3468 | 3.3468 | 0.8163 | 0.8163 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7088 | 1.7088 | 5.9485 | 5.9485 | 13.3318 | 13.3318 | 17.6171 | 17.6171 | 23.2495 | 23.2495 | 26.1473 | 26.1473 | 22.3994 | 22.3994 | 17.8417 | 17.8417 | 19.5128 | 19.5128 | 18.0752 | 18.0752 | 10.6235 | 10.6235 | 14.5264 | 14.5264 | 8.8771 | 8.8771 | 4.215 | 4.215 | 1.0681 | 1.0681 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5561 | 1.5561 | 5.8493 | 5.8493 | 12.5163 | 12.5163 | 18.8294 | 18.8294 | 29.1218 | 29.1218 | 27.7889 | 27.7889 | 28.7873 | 28.7873 | 18.9373 | 18.9373 | 20.31 | 20.31 | 22.3649 | 22.3649 | 16.3408 | 16.3408 | 10.5374 | 10.5374 | 8.0361 | 8.0361 | 3.9611 | 3.9611 | 0.83155 | 0.83155 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.052 | 2.052 | 5.7811 | 5.7811 | 11.7848 | 11.7848 | 16.9413 | 16.9413 | 21.5819 | 21.5819 | 24.5023 | 24.5023 | 26.325 | 26.325 | 23.4375 | 23.4375 | 20.569 | 20.569 | 18.9702 | 18.9702 | 17.3165 | 17.3165 | 12.5684 | 12.5684 | 7.3816 | 7.3816 | 3.3914 | 3.3914 | 0.69434 | 0.69434 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8308 | 1.8308 | 6.3977 | 6.3977 | 12.9336 | 12.9336 | 21.7859 | 21.7859 | 31.7241 | 31.7241 | 38.6796 | 38.6796 | 39.5241 | 39.5241 | 37.7212 | 37.7212 | 36.1183 | 36.1183 | 32.18 | 32.18 | 26.0515 | 26.0515 | 16.5783 | 16.5783 | 11.1452 | 11.1452 | 4.0517 | 4.0517 | 1.0375 | 1.0375 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6782 | 1.6782 | 6.8144 | 6.8144 | 10.9753 | 10.9753 | 17.4293 | 17.4293 | 28.9003 | 28.9003 | 32.7946 | 32.7946 | 35.3958 | 35.3958 | 31.9433 | 31.9433 | 34.5383 | 34.5383 | 30.2293 | 30.2293 | 23.6924 | 23.6924 | 15.6966 | 15.6966 | 8.6292 | 8.6292 | 3.6709 | 3.6709 | 0.93076 | 0.93076 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8994 | 1.8994 | 6.6567 | 6.6567 | 13.303 | 13.303 | 22.1253 | 22.1253 | 28.6661 | 28.6661 | 29.7988 | 29.7988 | 32.0108 | 32.0108 | 39.8824 | 39.8824 | 35.23 | 35.23 | 27.0805 | 27.0805 | 20.9846 | 20.9846 | 15.4347 | 15.4347 | 9.0792 | 9.0792 | 4.2546 | 4.2546 | 1.2358 | 1.2358 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2504 | 2.2504 | 5.656 | 5.656 | 11.1598 | 11.1598 | 15.1771 | 15.1771 | 14.776 | 14.776 | 21.496 | 21.496 | 21.3499 | 21.3499 | 19.9196 | 19.9196 | 18.4645 | 18.4645 | 21.4592 | 21.4592 | 13.5661 | 13.5661 | 11.9159 | 11.9159 | 8.6134 | 8.6134 | 3.3047 | 3.3047 | 0.64082 | 0.64082 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8842 | 1.8842 | 5.6347 | 5.6347 | 9.6991 | 9.6991 | 13.701 | 13.701 | 18.3506 | 18.3506 | 18.5599 | 18.5599 | 19.8612 | 19.8612 | 24.9913 | 24.9913 | 19.5178 | 19.5178 | 18.251 | 18.251 | 17.5587 | 17.5587 | 12.3465 | 12.3465 | 8.5896 | 8.5896 | 3.851 | 3.851 | 1.4036 | 1.4036 | 0 | 0 | 0 | 0 | 0 | 0
2022-05-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6629 | 1.6629 | 4.7248 | 4.7248 | 7.6091 | 7.6091 | 12.7201 | 12.7201 | 15.8916 | 15.8916 | 15.287 | 15.287 | 18.4345 | 18.4345 | 15.8379 | 15.8379 | 20.8203 | 20.8203 | 14.5678 | 14.5678 | 12.2931 | 12.2931 | 13.1779 | 13.1779 | 7.3268 | 7.3268 | 3.965 | 3.965 | 1.19 | 1.19 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8461 | 1.8461 | 5.2446 | 5.2446 | 11.5196 | 11.5196 | 16.9302 | 16.9302 | 21.8213 | 21.8213 | 28.7041 | 28.7041 | 22.1086 | 22.1086 | 26.7581 | 26.7581 | 19.1096 | 19.1096 | 18.7303 | 18.7303 | 16.3447 | 16.3447 | 14.1698 | 14.1698 | 8.22 | 8.22 | 3.6823 | 3.6823 | 1.0222 | 1.0222 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.335 | 1.335 | 3.7525 | 3.7525 | 7.3079 | 7.3079 | 11.2221 | 11.2221 | 17.5676 | 17.5676 | 19.2753 | 19.2753 | 22.5087 | 22.5087 | 15.6088 | 15.6088 | 21.4002 | 21.4002 | 19.6599 | 19.6599 | 16.637 | 16.637 | 14.4859 | 14.4859 | 9.4166 | 9.4166 | 3.8545 | 3.8545 | 1.3273 | 1.3273 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9453 | 1.9453 | 5.2724 | 5.2724 | 12.1476 | 12.1476 | 14.7944 | 14.7944 | 19.0145 | 19.0145 | 21.9603 | 21.9603 | 28.0569 | 28.0569 | 25.1205 | 25.1205 | 23.0913 | 23.0913 | 20.3708 | 20.3708 | 16.0637 | 16.0637 | 11.8602 | 11.8602 | 8.8525 | 8.8525 | 3.395 | 3.395 | 1.1901 | 1.1901 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.701 | 1.701 | 4.5297 | 4.5297 | 8.2772 | 8.2772 | 14.1006 | 14.1006 | 17.9394 | 17.9394 | 22.4145 | 22.4145 | 24.3818 | 24.3818 | 28.5556 | 28.5556 | 17.5376 | 17.5376 | 16.4531 | 16.4531 | 14.2426 | 14.2426 | 10.954 | 10.954 | 6.8091 | 6.8091 | 3.3652 | 3.3652 | 1.1366 | 1.1366 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1282 | 2.1282 | 5.425 | 5.425 | 8.1354 | 8.1354 | 13.31 | 13.31 | 19.4046 | 19.4046 | 17.2526 | 17.2526 | 21.1613 | 21.1613 | 25.7351 | 25.7351 | 28.2187 | 28.2187 | 25.5146 | 25.5146 | 20.031 | 20.031 | 13.583 | 13.583 | 9.0987 | 9.0987 | 4.1735 | 4.1735 | 1.3196 | 1.3196 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.099203 | 0.099203 | 1.9681 | 1.9681 | 5.9136 | 5.9136 | 13.1197 | 13.1197 | 19.0785 | 19.0785 | 21.4379 | 21.4379 | 23.9701 | 23.9701 | 27.6093 | 27.6093 | 31.3948 | 31.3948 | 29.0924 | 29.0924 | 29.1066 | 29.1066 | 20.1833 | 20.1833 | 17.5223 | 17.5223 | 10.3313 | 10.3313 | 4.0489 | 4.0489 | 1.2969 | 1.2969 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.229 | 0.229 | 2.5478 | 2.5478 | 7.2073 | 7.2073 | 12.9432 | 12.9432 | 21.4259 | 21.4259 | 23.7256 | 23.7256 | 30.4132 | 30.4132 | 24.7376 | 24.7376 | 26.0056 | 26.0056 | 16.9932 | 16.9932 | 17.5368 | 17.5368 | 15.6135 | 15.6135 | 12.809 | 12.809 | 6.9896 | 6.9896 | 4.2582 | 4.2582 | 0.97644 | 0.97644 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25184 | 0.25184 | 1.9452 | 1.9452 | 5.2578 | 5.2578 | 9.5735 | 9.5735 | 15.984 | 15.984 | 18.8498 | 18.8498 | 24.5772 | 24.5772 | 22.1579 | 22.1579 | 25.2081 | 25.2081 | 17.8396 | 17.8396 | 12.9009 | 12.9009 | 17.6876 | 17.6876 | 10.2545 | 10.2545 | 7.9261 | 7.9261 | 4.5695 | 4.5695 | 1.3273 | 1.3273 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19841 | 0.19841 | 2.174 | 2.174 | 5.223 | 5.223 | 11.0089 | 11.0089 | 16.1118 | 16.1118 | 25.1294 | 25.1294 | 27.575 | 27.575 | 33.3604 | 33.3604 | 26.4221 | 26.4221 | 28.2626 | 28.2626 | 28.3719 | 28.3719 | 19.6549 | 19.6549 | 15.547 | 15.547 | 8.5831 | 8.5831 | 2.9421 | 2.9421 | 1.3427 | 1.3427 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19074 | 0.19074 | 1.5867 | 1.5867 | 4.4175 | 4.4175 | 9.1412 | 9.1412 | 14.7633 | 14.7633 | 18.0354 | 18.0354 | 26.4419 | 26.4419 | 28.3184 | 28.3184 | 28.3428 | 28.3428 | 27.5607 | 27.5607 | 28.5193 | 28.5193 | 20.8866 | 20.8866 | 14.044 | 14.044 | 8.6128 | 8.6128 | 3.5951 | 3.5951 | 1.2358 | 1.2358 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23659 | 0.23659 | 1.7621 | 1.7621 | 5.149 | 5.149 | 10.1868 | 10.1868 | 18.108 | 18.108 | 21.8029 | 21.8029 | 22.4594 | 22.4594 | 33.0137 | 33.0137 | 30.6114 | 30.6114 | 26.0918 | 26.0918 | 20.0223 | 20.0223 | 21.9796 | 21.9796 | 17.5857 | 17.5857 | 10.5569 | 10.5569 | 3.4915 | 3.4915 | 1.1748 | 1.1748 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11446 | 0.11446 | 1.7546 | 1.7546 | 4.3727 | 4.3727 | 8.9577 | 8.9577 | 11.7705 | 11.7705 | 13.6772 | 13.6772 | 11.7279 | 11.7279 | 14.1947 | 14.1947 | 12.7484 | 12.7484 | 13.4299 | 13.4299 | 16.1137 | 16.1137 | 12.3474 | 12.3474 | 10.0943 | 10.0943 | 5.401 | 5.401 | 3.3398 | 3.3398 | 1.373 | 1.373 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41974 | 0.41974 | 1.5714 | 1.5714 | 4.8106 | 4.8106 | 7.9051 | 7.9051 | 14.2992 | 14.2992 | 20.9443 | 20.9443 | 25.3134 | 25.3134 | 17.8251 | 17.8251 | 18.2506 | 18.2506 | 21.8272 | 21.8272 | 19.2808 | 19.2808 | 15.1781 | 15.1781 | 12.8375 | 12.8375 | 6.6715 | 6.6715 | 4.0244 | 4.0244 | 1.4112 | 1.4112 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25176 | 0.25176 | 1.9681 | 1.9681 | 5.6505 | 5.6505 | 9.3885 | 9.3885 | 13.4649 | 13.4649 | 15.2913 | 15.2913 | 15.6718 | 15.6718 | 19.755 | 19.755 | 22.7462 | 22.7462 | 25.2083 | 25.2083 | 26.2905 | 26.2905 | 19.4707 | 19.4707 | 15.1424 | 15.1424 | 10.0199 | 10.0199 | 4.7341 | 4.7341 | 1.8232 | 1.8232 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20599 | 0.20599 | 2.1282 | 2.1282 | 6.6173 | 6.6173 | 13.8926 | 13.8926 | 22.3785 | 22.3785 | 29.3594 | 29.3594 | 32.8013 | 32.8013 | 31.7089 | 31.7089 | 28.0136 | 28.0136 | 20.672 | 20.672 | 20.3845 | 20.3845 | 17.8219 | 17.8219 | 15.9627 | 15.9627 | 10.0832 | 10.0832 | 4.601 | 4.601 | 1.5332 | 1.5332 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3052 | 0.3052 | 2.4867 | 2.4867 | 6.0307 | 6.0307 | 10.9049 | 10.9049 | 17.4299 | 17.4299 | 22.3972 | 22.3972 | 25.4747 | 25.4747 | 21.736 | 21.736 | 22.9966 | 22.9966 | 27.4097 | 27.4097 | 27.1513 | 27.1513 | 15.0697 | 15.0697 | 11.8442 | 11.8442 | 8.3068 | 8.3068 | 4.6213 | 4.6213 | 1.7622 | 1.7622 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2365 | 0.2365 | 1.9605 | 1.9605 | 4.9063 | 4.9063 | 9.6744 | 9.6744 | 15.779 | 15.779 | 20.3335 | 20.3335 | 28.1924 | 28.1924 | 23.1735 | 23.1735 | 19.5407 | 19.5407 | 17.9802 | 17.9802 | 16.4372 | 16.4372 | 13.6433 | 13.6433 | 12.9134 | 12.9134 | 5.491 | 5.491 | 2.938 | 2.938 | 1.068 | 1.068 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25176 | 0.25176 | 1.8765 | 1.8765 | 5.3391 | 5.3391 | 11.7828 | 11.7828 | 15.1517 | 15.1517 | 20.3175 | 20.3175 | 22.8572 | 22.8572 | 26.4691 | 26.4691 | 26.0154 | 26.0154 | 29.4414 | 29.4414 | 21.002 | 21.002 | 21.0888 | 21.0888 | 15.315 | 15.315 | 9.4143 | 9.4143 | 4.9051 | 4.9051 | 1.4799 | 1.4799 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22892 | 0.22892 | 2.0596 | 2.0596 | 5.7469 | 5.7469 | 9.8783 | 9.8783 | 14.8197 | 14.8197 | 22.2784 | 22.2784 | 21.5788 | 21.5788 | 28.6861 | 28.6861 | 26.3193 | 26.3193 | 24.1245 | 24.1245 | 22.7603 | 22.7603 | 19.2267 | 19.2267 | 15.9241 | 15.9241 | 9.8676 | 9.8676 | 4.2051 | 4.2051 | 1.5257 | 1.5257 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20608 | 0.20608 | 1.5638 | 1.5638 | 4.9372 | 4.9372 | 7.078 | 7.078 | 12.3953 | 12.3953 | 12.4863 | 12.4863 | 17.7205 | 17.7205 | 16.9671 | 16.9671 | 24.7871 | 24.7871 | 25.7597 | 25.7597 | 24.9652 | 24.9652 | 20.8388 | 20.8388 | 17.4765 | 17.4765 | 11.5262 | 11.5262 | 4.0119 | 4.0119 | 1.3807 | 1.3807 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076278 | 0.076278 | 1.6477 | 1.6477 | 4.7988 | 4.7988 | 11.881 | 11.881 | 15.1837 | 15.1837 | 24.7243 | 24.7243 | 32.4701 | 32.4701 | 31.5977 | 31.5977 | 30.8416 | 30.8416 | 28.4186 | 28.4186 | 29.6044 | 29.6044 | 23.5342 | 23.5342 | 18.6645 | 18.6645 | 9.5309 | 9.5309 | 4.9382 | 4.9382 | 2.0137 | 2.0137 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32054 | 0.32054 | 2.2045 | 2.2045 | 6.1195 | 6.1195 | 10.6981 | 10.6981 | 16.0654 | 16.0654 | 18.6204 | 18.6204 | 22.3431 | 22.3431 | 26.4503 | 26.4503 | 27.9778 | 27.9778 | 29.9985 | 29.9985 | 28.8538 | 28.8538 | 21.6753 | 21.6753 | 16.0443 | 16.0443 | 11.2869 | 11.2869 | 5.2652 | 5.2652 | 1.4036 | 1.4036 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37389 | 0.37389 | 2.2807 | 2.2807 | 6.4802 | 6.4802 | 12.5798 | 12.5798 | 17.6042 | 17.6042 | 22.4298 | 22.4298 | 25.155 | 25.155 | 27.5257 | 27.5257 | 28.9164 | 28.9164 | 25.4107 | 25.4107 | 21.1383 | 21.1383 | 20.2341 | 20.2341 | 14.6887 | 14.6887 | 7.4654 | 7.4654 | 4.4911 | 4.4911 | 1.0527 | 1.0527 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24417 | 0.24417 | 2.3647 | 2.3647 | 6.6522 | 6.6522 | 12.201 | 12.201 | 19.7681 | 19.7681 | 27.7414 | 27.7414 | 30.499 | 30.499 | 31.8784 | 31.8784 | 29.0135 | 29.0135 | 28.6763 | 28.6763 | 27.5486 | 27.5486 | 24.43 | 24.43 | 16.9339 | 16.9339 | 9.6499 | 9.6499 | 4.3016 | 4.3016 | 1.0375 | 1.0375 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40431 | 0.40431 | 2.296 | 2.296 | 6.6711 | 6.6711 | 13.885 | 13.885 | 21.2935 | 21.2935 | 27.1609 | 27.1609 | 27.6209 | 27.6209 | 31.741 | 31.741 | 31.8476 | 31.8476 | 26.1685 | 26.1685 | 25.8495 | 25.8495 | 23.0907 | 23.0907 | 18.0049 | 18.0049 | 12.1063 | 12.1063 | 5.3032 | 5.3032 | 1.8232 | 1.8232 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27468 | 0.27468 | 1.724 | 1.724 | 5.3699 | 5.3699 | 11.6104 | 11.6104 | 18.2821 | 18.2821 | 26.3577 | 26.3577 | 32.7048 | 32.7048 | 37.8376 | 37.8376 | 40.2393 | 40.2393 | 37.5453 | 37.5453 | 31.0885 | 31.0885 | 26.1419 | 26.1419 | 19.7012 | 19.7012 | 12.2607 | 12.2607 | 4.4613 | 4.4613 | 1.0221 | 1.0221 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14505 | 0.14505 | 1.4341 | 1.4341 | 4.7255 | 4.7255 | 8.8344 | 8.8344 | 14.5975 | 14.5975 | 16.355 | 16.355 | 20.3365 | 20.3365 | 23.3331 | 23.3331 | 25.1868 | 25.1868 | 29.3225 | 29.3225 | 21.7006 | 21.7006 | 19.3798 | 19.3798 | 14.8271 | 14.8271 | 8.9386 | 8.9386 | 3.9975 | 3.9975 | 1.1823 | 1.1823 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.091618 | 0.091618 | 2.1131 | 2.1131 | 5.6325 | 5.6325 | 10.0354 | 10.0354 | 14.3667 | 14.3667 | 20.1081 | 20.1081 | 20.0961 | 20.0961 | 22.1157 | 22.1157 | 17.0652 | 17.0652 | 19.0449 | 19.0449 | 24.3296 | 24.3296 | 17.0366 | 17.0366 | 8.6667 | 8.6667 | 5.7602 | 5.7602 | 4.617 | 4.617 | 1.2282 | 1.2282 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9299 | 1.9299 | 6.4848 | 6.4848 | 11.5092 | 11.5092 | 20.2174 | 20.2174 | 22.9864 | 22.9864 | 24.5767 | 24.5767 | 26.4382 | 26.4382 | 25.6094 | 25.6094 | 24.259 | 24.259 | 21.9511 | 21.9511 | 18.649 | 18.649 | 14.2223 | 14.2223 | 8.4324 | 8.4324 | 3.7156 | 3.7156 | 1.5409 | 1.5409 | 0 | 0 | 0 | 0 | 0 | 0
2022-06-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9605 | 1.9605 | 5.9259 | 5.9259 | 11.9099 | 11.9099 | 16.9256 | 16.9256 | 22.6151 | 22.6151 | 27.8309 | 27.8309 | 30.4885 | 30.4885 | 28.77 | 28.77 | 24.3754 | 24.3754 | 23.0241 | 23.0241 | 21.6975 | 21.6975 | 15.2029 | 15.2029 | 8.8401 | 8.8401 | 4.9817 | 4.9817 | 1.6019 | 1.6019 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2961 | 2.2961 | 5.8433 | 5.8433 | 10.9114 | 10.9114 | 17.1879 | 17.1879 | 22.4874 | 22.4874 | 19.3172 | 19.3172 | 16.4261 | 16.4261 | 21.7261 | 21.7261 | 20.1405 | 20.1405 | 25.5395 | 25.5395 | 17.1264 | 17.1264 | 12.6179 | 12.6179 | 9.198 | 9.198 | 4.8888 | 4.8888 | 1.0299 | 1.0299 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8765 | 1.8765 | 6.1449 | 6.1449 | 14.5784 | 14.5784 | 17.4872 | 17.4872 | 20.5929 | 20.5929 | 23.9067 | 23.9067 | 31.6633 | 31.6633 | 26.6078 | 26.6078 | 29.2747 | 29.2747 | 27.6201 | 27.6201 | 21.4875 | 21.4875 | 17.9343 | 17.9343 | 10.9412 | 10.9412 | 5.5025 | 5.5025 | 1.6706 | 1.6706 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3037 | 2.3037 | 6.1204 | 6.1204 | 15.2577 | 15.2577 | 21.0147 | 21.0147 | 26.109 | 26.109 | 28.4895 | 28.4895 | 33.2822 | 33.2822 | 33.1648 | 33.1648 | 30.4845 | 30.4845 | 25.7179 | 25.7179 | 23.6239 | 23.6239 | 19.5334 | 19.5334 | 11.2063 | 11.2063 | 4.7247 | 4.7247 | 1.6706 | 1.6706 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9147 | 1.9147 | 5.8132 | 5.8132 | 8.7221 | 8.7221 | 21.5744 | 21.5744 | 24.807 | 24.807 | 27.2033 | 27.2033 | 21.8546 | 21.8546 | 22.794 | 22.794 | 23.9364 | 23.9364 | 22.099 | 22.099 | 16.5605 | 16.5605 | 11.0454 | 11.0454 | 9.0653 | 9.0653 | 4.5483 | 4.5483 | 1.6553 | 1.6553 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1283 | 2.1283 | 4.9447 | 4.9447 | 9.6039 | 9.6039 | 14.8716 | 14.8716 | 19.0429 | 19.0429 | 24.5161 | 24.5161 | 28.2128 | 28.2128 | 35.5005 | 35.5005 | 36.8279 | 36.8279 | 26.6512 | 26.6512 | 25.0018 | 25.0018 | 16.9675 | 16.9675 | 9.1203 | 9.1203 | 5.1117 | 5.1117 | 1.8842 | 1.8842 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.441 | 2.441 | 6.7572 | 6.7572 | 13.8397 | 13.8397 | 22.3606 | 22.3606 | 25.9186 | 25.9186 | 30.0826 | 30.0826 | 33.3886 | 33.3886 | 32.6926 | 32.6926 | 34.7558 | 34.7558 | 33.266 | 33.266 | 27.8436 | 27.8436 | 19.476 | 19.476 | 11.3729 | 11.3729 | 4.6264 | 4.6264 | 1.6401 | 1.6401 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7545 | 1.7545 | 5.6964 | 5.6964 | 11.0642 | 11.0642 | 18.3121 | 18.3121 | 25.4338 | 25.4338 | 28.3838 | 28.3838 | 30.5753 | 30.5753 | 34.2436 | 34.2436 | 28.0246 | 28.0246 | 26.8344 | 26.8344 | 20.5947 | 20.5947 | 11.1023 | 11.1023 | 8.7307 | 8.7307 | 4.4991 | 4.4991 | 1.2892 | 1.2892 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6324 | 1.6324 | 4.2214 | 4.2214 | 9.8125 | 9.8125 | 11.9261 | 11.9261 | 16.5064 | 16.5064 | 18.4159 | 18.4159 | 18.5134 | 18.5134 | 17.5248 | 17.5248 | 20.8862 | 20.8862 | 17.5758 | 17.5758 | 18.1171 | 18.1171 | 16.4293 | 16.4293 | 10.7123 | 10.7123 | 4.6769 | 4.6769 | 1.5486 | 1.5486 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0063 | 2.0063 | 5.3298 | 5.3298 | 10.7128 | 10.7128 | 17.7678 | 17.7678 | 24.3142 | 24.3142 | 25.1604 | 25.1604 | 24.9734 | 24.9734 | 19.744 | 19.744 | 19.8744 | 19.8744 | 17.2084 | 17.2084 | 18.3057 | 18.3057 | 12.2319 | 12.2319 | 7.4735 | 7.4735 | 4.441 | 4.441 | 1.5791 | 1.5791 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7469 | 1.7469 | 5.586 | 5.586 | 10.3233 | 10.3233 | 16.7699 | 16.7699 | 19.8002 | 19.8002 | 24.076 | 24.076 | 21.6105 | 21.6105 | 23.6034 | 23.6034 | 24.75 | 24.75 | 25.2507 | 25.2507 | 23.1497 | 23.1497 | 18.3223 | 18.3223 | 11.542 | 11.542 | 5.3782 | 5.3782 | 1.5027 | 1.5027 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6935 | 1.6935 | 4.5713 | 4.5713 | 9.3099 | 9.3099 | 15.4118 | 15.4118 | 20.3535 | 20.3535 | 18.0542 | 18.0542 | 25.9345 | 25.9345 | 20.4839 | 20.4839 | 22.9042 | 22.9042 | 19.1347 | 19.1347 | 17.3379 | 17.3379 | 12.7793 | 12.7793 | 9.131 | 9.131 | 4.4215 | 4.4215 | 1.5409 | 1.5409 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6172 | 1.6172 | 4.5104 | 4.5104 | 8.8395 | 8.8395 | 14.1721 | 14.1721 | 15.7495 | 15.7495 | 20.7751 | 20.7751 | 17.3377 | 17.3377 | 22.4505 | 22.4505 | 22.8011 | 22.8011 | 22.5585 | 22.5585 | 17.4282 | 17.4282 | 10.3541 | 10.3541 | 8.998 | 8.998 | 4.3619 | 4.3619 | 1.6477 | 1.6477 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4264 | 1.4264 | 4.8722 | 4.8722 | 11.1483 | 11.1483 | 18.1891 | 18.1891 | 23.3709 | 23.3709 | 26.113 | 26.113 | 22.1385 | 22.1385 | 24.6974 | 24.6974 | 17.6856 | 17.6856 | 18.3439 | 18.3439 | 21.8348 | 21.8348 | 13.5232 | 13.5232 | 7.3955 | 7.3955 | 4.2006 | 4.2006 | 1.2359 | 1.2359 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8841 | 1.8841 | 5.217 | 5.217 | 10.3291 | 10.3291 | 14.8019 | 14.8019 | 19.455 | 19.455 | 20.2928 | 20.2928 | 17.2706 | 17.2706 | 15.9092 | 15.9092 | 19.3401 | 19.3401 | 15.9426 | 15.9426 | 15.92 | 15.92 | 11.072 | 11.072 | 7.9869 | 7.9869 | 3.7487 | 3.7487 | 1.2816 | 1.2816 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5181 | 1.5181 | 5.3691 | 5.3691 | 11.263 | 11.263 | 17.4018 | 17.4018 | 19.4449 | 19.4449 | 18.4531 | 18.4531 | 20.0297 | 20.0297 | 22.6388 | 22.6388 | 21.8332 | 21.8332 | 18.7435 | 18.7435 | 15.8504 | 15.8504 | 10.4143 | 10.4143 | 7.0307 | 7.0307 | 3.1688 | 3.1688 | 0.89258 | 0.89258 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7392 | 1.7392 | 4.5165 | 4.5165 | 8.779 | 8.779 | 13.9395 | 13.9395 | 17.7109 | 17.7109 | 22.0093 | 22.0093 | 21.6772 | 21.6772 | 22.8928 | 22.8928 | 24.6016 | 24.6016 | 25.2733 | 25.2733 | 18.7213 | 18.7213 | 11.851 | 11.851 | 7.6826 | 7.6826 | 4.3778 | 4.3778 | 1.1977 | 1.1977 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6477 | 1.6477 | 5.0139 | 5.0139 | 12.1256 | 12.1256 | 18.9995 | 18.9995 | 23.0242 | 23.0242 | 26.8449 | 26.8449 | 30.6319 | 30.6319 | 30.6607 | 30.6607 | 29.952 | 29.952 | 28.9857 | 28.9857 | 25.9519 | 25.9519 | 20.2686 | 20.2686 | 11.59 | 11.59 | 5.075 | 5.075 | 1.6401 | 1.6401 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8079 | 1.8079 | 6.0265 | 6.0265 | 12.2688 | 12.2688 | 19.1767 | 19.1767 | 26.4613 | 26.4613 | 27.6369 | 27.6369 | 35.2778 | 35.2778 | 36.7149 | 36.7149 | 34.8067 | 34.8067 | 33.5583 | 33.5583 | 23.496 | 23.496 | 16.8271 | 16.8271 | 8.2941 | 8.2941 | 3.5709 | 3.5709 | 1.3197 | 1.3197 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4494 | 1.4494 | 4.7432 | 4.7432 | 9.3127 | 9.3127 | 19.1692 | 19.1692 | 21.8765 | 21.8765 | 22.2012 | 22.2012 | 26.7238 | 26.7238 | 20.9564 | 20.9564 | 18.7442 | 18.7442 | 20.9185 | 20.9185 | 18.0998 | 18.0998 | 14.9338 | 14.9338 | 9.1398 | 9.1398 | 4.4158 | 4.4158 | 1.5409 | 1.5409 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3045 | 1.3045 | 4.2861 | 4.2861 | 10.0759 | 10.0759 | 14.6865 | 14.6865 | 19.9181 | 19.9181 | 13.1902 | 13.1902 | 19.4173 | 19.4173 | 22.5439 | 22.5439 | 22.4847 | 22.4847 | 24.2334 | 24.2334 | 18.0129 | 18.0129 | 14.6846 | 14.6846 | 9.3745 | 9.3745 | 4.135 | 4.135 | 1.0298 | 1.0298 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5409 | 1.5409 | 5.496 | 5.496 | 12.4113 | 12.4113 | 18.9428 | 18.9428 | 26.5917 | 26.5917 | 28.0847 | 28.0847 | 33.229 | 33.229 | 30.7442 | 30.7442 | 32.1641 | 32.1641 | 24.1002 | 24.1002 | 21.5122 | 21.5122 | 14.6426 | 14.6426 | 9.8902 | 9.8902 | 4.2558 | 4.2558 | 1.5257 | 1.5257 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3426 | 1.3426 | 4.6808 | 4.6808 | 9.3999 | 9.3999 | 18.55 | 18.55 | 22.6685 | 22.6685 | 27.0177 | 27.0177 | 24.9052 | 24.9052 | 21.815 | 21.815 | 16.2012 | 16.2012 | 11.7148 | 11.7148 | 13.1485 | 13.1485 | 10.2948 | 10.2948 | 10.3369 | 10.3369 | 4.6821 | 4.6821 | 1.4264 | 1.4264 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4951 | 1.4951 | 5.9521 | 5.9521 | 10.8744 | 10.8744 | 15.9134 | 15.9134 | 23.8765 | 23.8765 | 24.5596 | 24.5596 | 26.4034 | 26.4034 | 20.9058 | 20.9058 | 22.0057 | 22.0057 | 25.4219 | 25.4219 | 21.429 | 21.429 | 17.7423 | 17.7423 | 11.0327 | 11.0327 | 4.3189 | 4.3189 | 1.1519 | 1.1519 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0756 | 1.0756 | 3.8889 | 3.8889 | 9.157 | 9.157 | 14.1631 | 14.1631 | 16.3092 | 16.3092 | 16.7858 | 16.7858 | 17.1653 | 17.1653 | 17.8245 | 17.8245 | 14.5437 | 14.5437 | 12.1995 | 12.1995 | 7.5514 | 7.5514 | 11.4199 | 11.4199 | 7.1152 | 7.1152 | 3.2434 | 3.2434 | 0.78579 | 0.78579 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2891 | 1.2891 | 4.835 | 4.835 | 10.1559 | 10.1559 | 16.139 | 16.139 | 22.2495 | 22.2495 | 24.9825 | 24.9825 | 23.5217 | 23.5217 | 25.1008 | 25.1008 | 18.4837 | 18.4837 | 19.0032 | 19.0032 | 14.9994 | 14.9994 | 11.8631 | 11.8631 | 8.1988 | 8.1988 | 4.6301 | 4.6301 | 1.2129 | 1.2129 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4113 | 1.4113 | 4.0286 | 4.0286 | 7.5522 | 7.5522 | 10.5807 | 10.5807 | 16.2945 | 16.2945 | 18.113 | 18.113 | 20.79 | 20.79 | 20.0612 | 20.0612 | 19.7391 | 19.7391 | 17.8676 | 17.8676 | 14.5862 | 14.5862 | 8.8245 | 8.8245 | 6.9942 | 6.9942 | 3.0461 | 3.0461 | 0.93076 | 0.93076 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0756 | 1.0756 | 3.9772 | 3.9772 | 6.9929 | 6.9929 | 11.5495 | 11.5495 | 14.9536 | 14.9536 | 19.0056 | 19.0056 | 15.8579 | 15.8579 | 12.6486 | 12.6486 | 17.1241 | 17.1241 | 15.2002 | 15.2002 | 11.9237 | 11.9237 | 9.7985 | 9.7985 | 5.6364 | 5.6364 | 3.213 | 3.213 | 0.68667 | 0.68667 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3045 | 1.3045 | 5.3051 | 5.3051 | 11.5536 | 11.5536 | 17.1501 | 17.1501 | 13.9291 | 13.9291 | 25.8879 | 25.8879 | 26.1538 | 26.1538 | 23.706 | 23.706 | 20.1595 | 20.1595 | 19.0662 | 19.0662 | 14.1646 | 14.1646 | 10.2629 | 10.2629 | 8.3298 | 8.3298 | 4.0415 | 4.0415 | 1.0603 | 1.0603 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1367 | 1.1367 | 4.2801 | 4.2801 | 9.6391 | 9.6391 | 15.0357 | 15.0357 | 17.8593 | 17.8593 | 18.8371 | 18.8371 | 17.4603 | 17.4603 | 24.9519 | 24.9519 | 23.6297 | 23.6297 | 11.8112 | 11.8112 | 13.755 | 13.755 | 10.1875 | 10.1875 | 5.3938 | 5.3938 | 4.0643 | 4.0643 | 0.68658 | 0.68658 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1595 | 1.1595 | 3.9081 | 3.9081 | 10.7129 | 10.7129 | 16.2253 | 16.2253 | 18.1338 | 18.1338 | 18.2594 | 18.2594 | 20.0879 | 20.0879 | 26.7202 | 26.7202 | 20.3598 | 20.3598 | 15.8716 | 15.8716 | 16.9337 | 16.9337 | 10.8858 | 10.8858 | 10.0003 | 10.0003 | 3.4092 | 3.4092 | 0.81621 | 0.81621 | 0 | 0 | 0 | 0 | 0 | 0
2022-07-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3807 | 1.3807 | 5.4639 | 5.4639 | 13.346 | 13.346 | 21.8052 | 21.8052 | 23.5251 | 23.5251 | 21.3196 | 21.3196 | 28.5009 | 28.5009 | 31.4189 | 31.4189 | 26.1398 | 26.1398 | 24.4198 | 24.4198 | 16.7213 | 16.7213 | 11.6048 | 11.6048 | 7.9107 | 7.9107 | 4.1381 | 4.1381 | 0.99161 | 0.99161 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2281 | 1.2281 | 5.0502 | 5.0502 | 11.6138 | 11.6138 | 19.1413 | 19.1413 | 24.1674 | 24.1674 | 28.2359 | 28.2359 | 24.3518 | 24.3518 | 31.5224 | 31.5224 | 26.6206 | 26.6206 | 18.17 | 18.17 | 20.0286 | 20.0286 | 14.7662 | 14.7662 | 9.2254 | 9.2254 | 2.815 | 2.815 | 0.73994 | 0.73994 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0527 | 1.0527 | 3.6448 | 3.6448 | 8.5199 | 8.5199 | 15.285 | 15.285 | 20.3088 | 20.3088 | 22.7958 | 22.7958 | 24.3464 | 24.3464 | 27.2903 | 27.2903 | 21.8524 | 21.8524 | 22.2175 | 22.2175 | 19.4985 | 19.4985 | 12.4172 | 12.4172 | 7.3533 | 7.3533 | 3.3634 | 3.3634 | 0.53394 | 0.53394 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0832 | 1.0832 | 3.7772 | 3.7772 | 9.2413 | 9.2413 | 15.9886 | 15.9886 | 19.8316 | 19.8316 | 23.7179 | 23.7179 | 22.6414 | 22.6414 | 23.7217 | 23.7217 | 27.3379 | 27.3379 | 24.5112 | 24.5112 | 19.0584 | 19.0584 | 13.4163 | 13.4163 | 9.5825 | 9.5825 | 3.5601 | 3.5601 | 0.58755 | 0.58755 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1518 | 1.1518 | 5.0565 | 5.0565 | 11.7881 | 11.7881 | 17.1864 | 17.1864 | 25.6281 | 25.6281 | 26.4356 | 26.4356 | 16.9488 | 16.9488 | 20.5182 | 20.5182 | 22.9699 | 22.9699 | 26.9353 | 26.9353 | 22.7262 | 22.7262 | 15.3057 | 15.3057 | 9.9099 | 9.9099 | 3.4676 | 3.4676 | 0.61039 | 0.61039 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58738 | 0.58738 | 4.6828 | 4.6828 | 10.1382 | 10.1382 | 17.92 | 17.92 | 28.1706 | 28.1706 | 29.5082 | 29.5082 | 32.6845 | 32.6845 | 25.5734 | 25.5734 | 26.4461 | 26.4461 | 27.8993 | 27.8993 | 21.5458 | 21.5458 | 15.0777 | 15.0777 | 9.7514 | 9.7514 | 3.599 | 3.599 | 0.55704 | 0.55704 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93067 | 0.93067 | 3.9531 | 3.9531 | 9.5727 | 9.5727 | 16.264 | 16.264 | 22.1167 | 22.1167 | 25.9884 | 25.9884 | 29.5171 | 29.5171 | 30.4742 | 30.4742 | 38.4228 | 38.4228 | 27.4808 | 27.4808 | 25.2578 | 25.2578 | 17.6454 | 17.6454 | 10.6768 | 10.6768 | 3.586 | 3.586 | 0.61789 | 0.61789 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89249 | 0.89249 | 4.2367 | 4.2367 | 10.1052 | 10.1052 | 15.5095 | 15.5095 | 21.5258 | 21.5258 | 27.2711 | 27.2711 | 27.5216 | 27.5216 | 35.1634 | 35.1634 | 22.8682 | 22.8682 | 23.4411 | 23.4411 | 22.8435 | 22.8435 | 12.0503 | 12.0503 | 7.3978 | 7.3978 | 2.8038 | 2.8038 | 0.29753 | 0.29753 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74761 | 0.74761 | 3.8538 | 3.8538 | 10.3956 | 10.3956 | 15.5627 | 15.5627 | 22.9171 | 22.9171 | 19.7945 | 19.7945 | 22.9437 | 22.9437 | 30.8737 | 30.8737 | 26.0344 | 26.0344 | 15.6739 | 15.6739 | 15.9759 | 15.9759 | 11.4494 | 11.4494 | 6.057 | 6.057 | 3.2255 | 3.2255 | 0.45775 | 0.45775 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70943 | 0.70943 | 2.9091 | 2.9091 | 8.6877 | 8.6877 | 14.5004 | 14.5004 | 17.7437 | 17.7437 | 21.9763 | 21.9763 | 26.4118 | 26.4118 | 23.9888 | 23.9888 | 16.3282 | 16.3282 | 13.8044 | 13.8044 | 12.553 | 12.553 | 11.6673 | 11.6673 | 6.0732 | 6.0732 | 3.0091 | 3.0091 | 0.38914 | 0.38914 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63315 | 0.63315 | 3.8972 | 3.8972 | 7.8667 | 7.8667 | 17.0574 | 17.0574 | 21.4589 | 21.4589 | 19.4843 | 19.4843 | 18.1877 | 18.1877 | 14.0727 | 14.0727 | 24.5889 | 24.5889 | 14.2103 | 14.2103 | 19.1583 | 19.1583 | 12.3543 | 12.3543 | 8.0238 | 8.0238 | 3.1839 | 3.1839 | 0.35855 | 0.35855 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74761 | 0.74761 | 2.8318 | 2.8318 | 8.5742 | 8.5742 | 16.2332 | 16.2332 | 21.239 | 21.239 | 28.1979 | 28.1979 | 32.6315 | 32.6315 | 35.5059 | 35.5059 | 28.9604 | 28.9604 | 18.5191 | 18.5191 | 16.6821 | 16.6821 | 10.2865 | 10.2865 | 4.9879 | 4.9879 | 2.2024 | 2.2024 | 0.14497 | 0.14497 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5492 | 0.5492 | 2.9365 | 2.9365 | 8.9584 | 8.9584 | 14.4965 | 14.4965 | 20.8217 | 20.8217 | 28.0695 | 28.0695 | 31.0737 | 31.0737 | 26.6386 | 26.6386 | 23.4291 | 23.4291 | 20.0128 | 20.0128 | 20.9308 | 20.9308 | 13.9417 | 13.9417 | 10.8379 | 10.8379 | 3.3448 | 3.3448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4044 | 0.4044 | 2.9387 | 2.9387 | 7.7019 | 7.7019 | 13.3054 | 13.3054 | 16.9193 | 16.9193 | 19.9906 | 19.9906 | 23.1942 | 23.1942 | 21.5383 | 21.5383 | 18.1843 | 18.1843 | 21.9153 | 21.9153 | 17.1363 | 17.1363 | 14.3297 | 14.3297 | 7.4769 | 7.4769 | 2.6787 | 2.6787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47301 | 0.47301 | 2.4416 | 2.4416 | 6.4203 | 6.4203 | 11.117 | 11.117 | 16.6368 | 16.6368 | 18.3664 | 18.3664 | 18.6822 | 18.6822 | 18.6437 | 18.6437 | 23.8442 | 23.8442 | 19.5244 | 19.5244 | 14.1842 | 14.1842 | 8.7568 | 8.7568 | 5.8421 | 5.8421 | 2.1895 | 2.1895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38914 | 0.38914 | 3.0426 | 3.0426 | 8.4862 | 8.4862 | 12.5364 | 12.5364 | 19.2485 | 19.2485 | 18.3067 | 18.3067 | 25.8073 | 25.8073 | 8.5877 | 8.5877 | 23.1324 | 23.1324 | 19.0971 | 19.0971 | 16.4174 | 16.4174 | 13.9871 | 13.9871 | 8.1894 | 8.1894 | 2.5452 | 2.5452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28227 | 0.28227 | 2.7001 | 2.7001 | 7.1444 | 7.1444 | 12.7285 | 12.7285 | 16.2591 | 16.2591 | 16.9999 | 16.9999 | 18.9658 | 18.9658 | 20.3716 | 20.3716 | 17.6646 | 17.6646 | 15.8622 | 15.8622 | 16.3182 | 16.3182 | 12.0344 | 12.0344 | 7.5587 | 7.5587 | 2.8084 | 2.8084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19074 | 0.19074 | 3.9444 | 3.9444 | 10.3628 | 10.3628 | 15.8169 | 15.8169 | 19.9838 | 19.9838 | 27.481 | 27.481 | 28.0041 | 28.0041 | 30.5374 | 30.5374 | 30.6386 | 30.6386 | 17.6097 | 17.6097 | 18.9363 | 18.9363 | 14.7621 | 14.7621 | 6.9616 | 6.9616 | 2.1959 | 2.1959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.584 | 2.584 | 7.9016 | 7.9016 | 12.7652 | 12.7652 | 15.0108 | 15.0108 | 14.3711 | 14.3711 | 18.4917 | 18.4917 | 20.0772 | 20.0772 | 13.8149 | 13.8149 | 9.2876 | 9.2876 | 9.6197 | 9.6197 | 9.5407 | 9.5407 | 6.1787 | 6.1787 | 2.0783 | 2.0783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5166 | 3.5166 | 6.1461 | 6.1461 | 12.1625 | 12.1625 | 13.8409 | 13.8409 | 13.8171 | 13.8171 | 10.933 | 10.933 | 13.6268 | 13.6268 | 16.4574 | 16.4574 | 11.7626 | 11.7626 | 10.9315 | 10.9315 | 8.0499 | 8.0499 | 6.6687 | 6.6687 | 2.1327 | 2.1327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0579 | 3.0579 | 8.5434 | 8.5434 | 16.7527 | 16.7527 | 17.8323 | 17.8323 | 24.372 | 24.372 | 26.691 | 26.691 | 21.3563 | 21.3563 | 25.7665 | 25.7665 | 18.2772 | 18.2772 | 16.1059 | 16.1059 | 10.237 | 10.237 | 5.3449 | 5.3449 | 2.1549 | 2.1549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6024 | 2.6024 | 7.8501 | 7.8501 | 10.2434 | 10.2434 | 15.793 | 15.793 | 15.0633 | 15.0633 | 17.8727 | 17.8727 | 20.2101 | 20.2101 | 23.1986 | 23.1986 | 22.5122 | 22.5122 | 20.0127 | 20.0127 | 13.9326 | 13.9326 | 7.1999 | 7.1999 | 2.1736 | 2.1736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2398 | 3.2398 | 7.5432 | 7.5432 | 11.6112 | 11.6112 | 15.4218 | 15.4218 | 19.1177 | 19.1177 | 21.5185 | 21.5185 | 24.3475 | 24.3475 | 24.5062 | 24.5062 | 22.2725 | 22.2725 | 18.2871 | 18.2871 | 15.0186 | 15.0186 | 8.5136 | 8.5136 | 1.9916 | 1.9916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7125 | 2.7125 | 7.7229 | 7.7229 | 13.7163 | 13.7163 | 13.606 | 13.606 | 13.9062 | 13.9062 | 15.2341 | 15.2341 | 18.626 | 18.626 | 23.851 | 23.851 | 23.5553 | 23.5553 | 18.465 | 18.465 | 13.6281 | 13.6281 | 6.9784 | 6.9784 | 1.89 | 1.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8396 | 2.8396 | 8.7032 | 8.7032 | 13.9687 | 13.9687 | 20.9111 | 20.9111 | 19.7714 | 19.7714 | 25.8132 | 25.8132 | 22.1444 | 22.1444 | 20.9421 | 20.9421 | 20.2038 | 20.2038 | 13.36 | 13.36 | 7.5504 | 7.5504 | 3.4531 | 3.4531 | 1.5432 | 1.5432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0949 | 3.0949 | 8.9612 | 8.9612 | 15.5128 | 15.5128 | 21.1756 | 21.1756 | 19.8084 | 19.8084 | 19.1538 | 19.1538 | 22.1886 | 22.1886 | 21.1722 | 21.1722 | 13.0116 | 13.0116 | 16.0594 | 16.0594 | 15.0642 | 15.0642 | 8.6149 | 8.6149 | 1.8747 | 1.8747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5265 | 2.5265 | 8.9408 | 8.9408 | 13.35 | 13.35 | 15.4896 | 15.4896 | 17.4488 | 17.4488 | 22.9358 | 22.9358 | 22.2216 | 22.2216 | 21.795 | 21.795 | 16.7765 | 16.7765 | 14.3484 | 14.3484 | 11.4551 | 11.4551 | 6.109 | 6.109 | 1.3557 | 1.3557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7417 | 2.7417 | 6.3027 | 6.3027 | 11.7296 | 11.7296 | 17.5775 | 17.5775 | 18.7788 | 18.7788 | 21.1477 | 21.1477 | 23.8858 | 23.8858 | 17.3783 | 17.3783 | 18.0447 | 18.0447 | 17.8428 | 17.8428 | 9.7797 | 9.7797 | 5.8718 | 5.8718 | 0.9316 | 0.9316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9608 | 2.9608 | 7.6322 | 7.6322 | 14.0599 | 14.0599 | 20.7964 | 20.7964 | 23.7167 | 23.7167 | 24.6437 | 24.6437 | 22.1477 | 22.1477 | 20.6323 | 20.6323 | 20.7174 | 20.7174 | 15.5859 | 15.5859 | 10.7103 | 10.7103 | 6.3031 | 6.3031 | 1.3193 | 1.3193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2334 | 1.2334 | 4.6349 | 4.6349 | 11.5575 | 11.5575 | 17.0236 | 17.0236 | 17.7316 | 17.7316 | 23.0404 | 23.0404 | 13.9218 | 13.9218 | 19.4549 | 19.4549 | 5.7846 | 5.7846 | 7.2418 | 7.2418 | 8.1072 | 8.1072 | 4.8975 | 4.8975 | 1.2762 | 1.2762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9859 | 1.9859 | 6.4094 | 6.4094 | 13.0617 | 13.0617 | 18.912 | 18.912 | 20.2515 | 20.2515 | 17.1595 | 17.1595 | 17.2601 | 17.2601 | 16.5647 | 16.5647 | 15.1913 | 15.1913 | 12.3643 | 12.3643 | 8.2694 | 8.2694 | 5.6982 | 5.6982 | 1.1802 | 1.1802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-08-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6031 | 2.6031 | 8.7941 | 8.7941 | 15.4267 | 15.4267 | 23.4603 | 23.4603 | 21.6578 | 21.6578 | 18.7369 | 18.7369 | 19.6066 | 19.6066 | 19.4119 | 19.4119 | 9.704 | 9.704 | 11.0422 | 11.0422 | 8.5129 | 8.5129 | 5.2826 | 5.2826 | 0.89713 | 0.89713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9253 | 2.9253 | 10.61 | 10.61 | 17.4348 | 17.4348 | 25.02 | 25.02 | 29.5513 | 29.5513 | 31.7385 | 31.7385 | 31.128 | 31.128 | 26.7775 | 26.7775 | 25.5901 | 25.5901 | 21.1136 | 21.1136 | 10.8419 | 10.8419 | 4.9978 | 4.9978 | 1.022 | 1.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9372 | 2.9372 | 10.8076 | 10.8076 | 19.4515 | 19.4515 | 25.3736 | 25.3736 | 24.5692 | 24.5692 | 25.937 | 25.937 | 22.1501 | 22.1501 | 21.1438 | 21.1438 | 21.3287 | 21.3287 | 14.5087 | 14.5087 | 9.7073 | 9.7073 | 4.7058 | 4.7058 | 0.65683 | 0.65683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3767 | 2.3767 | 7.8536 | 7.8536 | 14.0999 | 14.0999 | 18.156 | 18.156 | 19.2622 | 19.2622 | 18.1882 | 18.1882 | 14.249 | 14.249 | 13.5149 | 13.5149 | 10.5636 | 10.5636 | 11.3368 | 11.3368 | 7.9516 | 7.9516 | 3.6963 | 3.6963 | 0.71667 | 0.71667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0957 | 2.0957 | 5.3705 | 5.3705 | 9.3788 | 9.3788 | 11.3704 | 11.3704 | 15.1023 | 15.1023 | 15.1951 | 15.1951 | 12.2043 | 12.2043 | 9.1667 | 9.1667 | 9.3658 | 9.3658 | 11.6684 | 11.6684 | 5.877 | 5.877 | 3.6736 | 3.6736 | 0.70951 | 0.70951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8218 | 1.8218 | 4.6918 | 4.6918 | 8.5275 | 8.5275 | 11.8768 | 11.8768 | 13.0452 | 13.0452 | 13.3505 | 13.3505 | 9.5142 | 9.5142 | 11.0653 | 11.0653 | 9.8346 | 9.8346 | 9.8933 | 9.8933 | 6.4883 | 6.4883 | 4.7684 | 4.7684 | 0.64849 | 0.64849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3945 | 2.3945 | 6.4972 | 6.4972 | 16.0743 | 16.0743 | 24.4595 | 24.4595 | 24.705 | 24.705 | 24.7166 | 24.7166 | 22.5817 | 22.5817 | 20.1855 | 20.1855 | 14.0188 | 14.0188 | 17.2561 | 17.2561 | 10.9035 | 10.9035 | 5.189 | 5.189 | 0.63315 | 0.63315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2674 | 2.2674 | 8.1751 | 8.1751 | 12.7187 | 12.7187 | 20.3279 | 20.3279 | 25.1072 | 25.1072 | 21.9346 | 21.9346 | 21.9483 | 21.9483 | 20.2187 | 20.2187 | 16.2806 | 16.2806 | 16.458 | 16.458 | 11.4503 | 11.4503 | 4.8642 | 4.8642 | 0.39673 | 0.39673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2204 | 1.2204 | 5.3195 | 5.3195 | 7.7704 | 7.7704 | 13.2955 | 13.2955 | 16.5131 | 16.5131 | 17.8137 | 17.8137 | 21.3907 | 21.3907 | 20.4805 | 20.4805 | 12.3555 | 12.3555 | 13.541 | 13.541 | 10.453 | 10.453 | 4.1273 | 4.1273 | 0.39681 | 0.39681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8269 | 1.8269 | 8.3633 | 8.3633 | 11.5347 | 11.5347 | 14.2338 | 14.2338 | 20.9578 | 20.9578 | 14.1169 | 14.1169 | 20.4385 | 20.4385 | 19.7784 | 19.7784 | 14.4403 | 14.4403 | 11.5541 | 11.5541 | 11.246 | 11.246 | 3.9174 | 3.9174 | 0.2365 | 0.2365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7505 | 1.7505 | 8.2366 | 8.2366 | 16.1834 | 16.1834 | 21.6923 | 21.6923 | 21.6896 | 21.6896 | 21.2011 | 21.2011 | 25.62 | 25.62 | 23.6693 | 23.6693 | 19.5671 | 19.5671 | 14.8357 | 14.8357 | 8.4553 | 8.4553 | 3.9847 | 3.9847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5298 | 1.5298 | 7.5121 | 7.5121 | 16.8334 | 16.8334 | 21.6919 | 21.6919 | 23.3228 | 23.3228 | 26.6272 | 26.6272 | 29.8808 | 29.8808 | 29.199 | 29.199 | 23.9207 | 23.9207 | 18.9619 | 18.9619 | 10.3047 | 10.3047 | 5.8369 | 5.8369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1672 | 1.1672 | 6.556 | 6.556 | 14.0523 | 14.0523 | 16.3896 | 16.3896 | 20.4564 | 20.4564 | 22.1834 | 22.1834 | 22.5587 | 22.5587 | 25.8447 | 25.8447 | 16.4618 | 16.4618 | 13.3302 | 13.3302 | 11.4128 | 11.4128 | 4.3023 | 4.3023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8223 | 1.8223 | 9.1182 | 9.1182 | 17.4183 | 17.4183 | 24.674 | 24.674 | 27.5734 | 27.5734 | 33.7882 | 33.7882 | 36.9967 | 36.9967 | 31.3848 | 31.3848 | 23.0513 | 23.0513 | 22.62 | 22.62 | 14.8428 | 14.8428 | 5.4417 | 5.4417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6271 | 1.6271 | 7.1629 | 7.1629 | 14.1292 | 14.1292 | 18.681 | 18.681 | 23.9436 | 23.9436 | 32.8037 | 32.8037 | 24.5855 | 24.5855 | 28.3983 | 28.3983 | 20.0082 | 20.0082 | 13.3716 | 13.3716 | 11.9615 | 11.9615 | 4.8353 | 4.8353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4441 | 1.4441 | 8.0429 | 8.0429 | 15.7918 | 15.7918 | 22.2706 | 22.2706 | 22.1216 | 22.1216 | 25.2444 | 25.2444 | 27.2351 | 27.2351 | 26.4056 | 26.4056 | 19.7116 | 19.7116 | 11.9309 | 11.9309 | 9.079 | 9.079 | 3.6561 | 3.6561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90497 | 0.90497 | 3.836 | 3.836 | 7.4173 | 7.4173 | 9.4512 | 9.4512 | 11.6173 | 11.6173 | 11.1255 | 11.1255 | 16.8096 | 16.8096 | 16.3224 | 16.3224 | 14.2644 | 14.2644 | 12.4481 | 12.4481 | 10.4633 | 10.4633 | 4.0329 | 4.0329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99119 | 0.99119 | 5.3217 | 5.3217 | 11.0182 | 11.0182 | 19.0026 | 19.0026 | 21.8348 | 21.8348 | 23.1274 | 23.1274 | 22.6505 | 22.6505 | 25.0151 | 25.0151 | 21.6717 | 21.6717 | 15.0768 | 15.0768 | 10.7055 | 10.7055 | 3.6334 | 3.6334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0914 | 1.0914 | 6.0451 | 6.0451 | 8.4504 | 8.4504 | 12.9855 | 12.9855 | 18.2027 | 18.2027 | 23.6405 | 23.6405 | 20.7539 | 20.7539 | 19.919 | 19.919 | 14.1962 | 14.1962 | 13.1881 | 13.1881 | 6.9817 | 6.9817 | 3.2856 | 3.2856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66636 | 0.66636 | 4.9202 | 4.9202 | 9.7459 | 9.7459 | 16.7675 | 16.7675 | 23.9275 | 23.9275 | 23.3219 | 23.3219 | 21.2301 | 21.2301 | 21.6172 | 21.6172 | 16.7115 | 16.7115 | 16.6058 | 16.6058 | 8.8066 | 8.8066 | 2.8499 | 2.8499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76168 | 0.76168 | 6.1842 | 6.1842 | 9.8351 | 9.8351 | 14.7383 | 14.7383 | 16.5972 | 16.5972 | 21.3373 | 21.3373 | 21.7423 | 21.7423 | 17.1731 | 17.1731 | 13.8311 | 13.8311 | 11.1251 | 11.1251 | 8.8631 | 8.8631 | 2.3605 | 2.3605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71313 | 0.71313 | 4.7022 | 4.7022 | 9.8905 | 9.8905 | 17.1136 | 17.1136 | 15.243 | 15.243 | 17.0581 | 17.0581 | 16.8147 | 16.8147 | 19.3122 | 19.3122 | 18.042 | 18.042 | 13.8268 | 13.8268 | 7.3082 | 7.3082 | 3.2431 | 3.2431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73496 | 0.73496 | 4.2763 | 4.2763 | 10.0915 | 10.0915 | 17.92 | 17.92 | 21.8219 | 21.8219 | 19.8106 | 19.8106 | 10.9944 | 10.9944 | 16.0235 | 16.0235 | 13.2515 | 13.2515 | 16.2371 | 16.2371 | 8.952 | 8.952 | 2.6568 | 2.6568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46399 | 0.46399 | 4.8715 | 4.8715 | 10.594 | 10.594 | 15.8777 | 15.8777 | 21.5087 | 21.5087 | 20.6918 | 20.6918 | 20.4594 | 20.4594 | 21.783 | 21.783 | 14.7788 | 14.7788 | 11.5239 | 11.5239 | 7.1018 | 7.1018 | 2.9041 | 2.9041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62801 | 0.62801 | 7.4021 | 7.4021 | 15.5228 | 15.5228 | 23.4946 | 23.4946 | 30.9609 | 30.9609 | 33.9063 | 33.9063 | 26.0443 | 26.0443 | 24.2288 | 24.2288 | 17.6222 | 17.6222 | 12.1041 | 12.1041 | 6.6253 | 6.6253 | 1.9104 | 1.9104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31936 | 0.31936 | 3.8876 | 3.8876 | 10.944 | 10.944 | 16.6453 | 16.6453 | 24.4545 | 24.4545 | 14.8011 | 14.8011 | 17.5899 | 17.5899 | 21.1525 | 21.1525 | 20.6692 | 20.6692 | 14.212 | 14.212 | 9.5769 | 9.5769 | 2.3593 | 2.3593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0329 | 6.0329 | 14.6924 | 14.6924 | 20.9444 | 20.9444 | 21.6035 | 21.6035 | 25.6761 | 25.6761 | 18.3802 | 18.3802 | 18.2804 | 18.2804 | 18.0338 | 18.0338 | 13.2909 | 13.2909 | 8.7462 | 8.7462 | 2.0278 | 2.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6523 | 6.6523 | 11.5849 | 11.5849 | 16.0028 | 16.0028 | 18.0969 | 18.0969 | 17.4706 | 17.4706 | 21.5042 | 21.5042 | 20.0268 | 20.0268 | 14.9657 | 14.9657 | 11.7249 | 11.7249 | 6.8622 | 6.8622 | 1.7879 | 1.7879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3163 | 6.3163 | 13.9791 | 13.9791 | 20.8575 | 20.8575 | 23.5283 | 23.5283 | 26.0831 | 26.0831 | 26.6392 | 26.6392 | 26.1216 | 26.1216 | 25.5487 | 25.5487 | 17.7891 | 17.7891 | 7.7736 | 7.7736 | 1.6578 | 1.6578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6876 | 4.6876 | 8.5513 | 8.5513 | 12.4822 | 12.4822 | 16.3714 | 16.3714 | 22.9478 | 22.9478 | 20.7417 | 20.7417 | 19.7401 | 19.7401 | 17.4272 | 17.4272 | 13.3078 | 13.3078 | 7.2524 | 7.2524 | 1.5222 | 1.5222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-09-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2106 | 6.2106 | 14.2554 | 14.2554 | 21.255 | 21.255 | 24.9836 | 24.9836 | 11.1252 | 11.1252 | 15.7286 | 15.7286 | 15.0699 | 15.0699 | 14.7262 | 14.7262 | 13.2567 | 13.2567 | 6.3381 | 6.3381 | 1.332 | 1.332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4496 | 4.4496 | 10.6297 | 10.6297 | 13.1214 | 13.1214 | 15.41 | 15.41 | 18.2888 | 18.2888 | 18.4777 | 18.4777 | 25.6134 | 25.6134 | 20.1691 | 20.1691 | 13.3071 | 13.3071 | 5.6129 | 5.6129 | 0.88617 | 0.88617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6519 | 4.6519 | 8.7955 | 8.7955 | 16.2583 | 16.2583 | 17.7945 | 17.7945 | 18.44 | 18.44 | 20.6206 | 20.6206 | 12.9003 | 12.9003 | 11.9007 | 11.9007 | 12.1211 | 12.1211 | 7.3286 | 7.3286 | 0.65616 | 0.65616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4157 | 5.4157 | 11.8156 | 11.8156 | 13.9699 | 13.9699 | 15.4867 | 15.4867 | 14.7536 | 14.7536 | 19.6701 | 19.6701 | 16.6627 | 16.6627 | 15.3543 | 15.3543 | 10.9422 | 10.9422 | 6.6722 | 6.6722 | 0.64124 | 0.64124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2359 | 4.2359 | 11.4979 | 11.4979 | 14.4597 | 14.4597 | 13.4503 | 13.4503 | 19.8234 | 19.8234 | 19.6096 | 19.6096 | 17.9141 | 17.9141 | 14.7685 | 14.7685 | 11.8264 | 11.8264 | 6.2195 | 6.2195 | 0.465 | 0.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.69 | 2.69 | 8.3128 | 8.3128 | 13.6718 | 13.6718 | 20.7385 | 20.7385 | 28.2947 | 28.2947 | 24.9638 | 24.9638 | 21.2798 | 21.2798 | 18.3411 | 18.3411 | 12.648 | 12.648 | 6.2772 | 6.2772 | 0.22327 | 0.22327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3496 | 4.3496 | 10.8834 | 10.8834 | 9.4101 | 9.4101 | 15.1278 | 15.1278 | 18.4112 | 18.4112 | 17.2051 | 17.2051 | 20.2611 | 20.2611 | 15.3036 | 15.3036 | 12.4477 | 12.4477 | 3.9934 | 3.9934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.661 | 2.661 | 5.5256 | 5.5256 | 9.6863 | 9.6863 | 14.3191 | 14.3191 | 12.6291 | 12.6291 | 13.4905 | 13.4905 | 15.0111 | 15.0111 | 9.9126 | 9.9126 | 7.88 | 7.88 | 4.4882 | 4.4882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.514 | 3.514 | 8.1401 | 8.1401 | 13.5912 | 13.5912 | 16.1666 | 16.1666 | 18.407 | 18.407 | 17.2794 | 17.2794 | 10.8254 | 10.8254 | 9.6348 | 9.6348 | 8.4169 | 8.4169 | 3.7222 | 3.7222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2816 | 5.2816 | 13.9642 | 13.9642 | 20.9432 | 20.9432 | 27.1283 | 27.1283 | 18.4809 | 18.4809 | 16.3411 | 16.3411 | 16.9305 | 16.9305 | 12.0111 | 12.0111 | 8.6826 | 8.6826 | 5.6652 | 5.6652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8534 | 4.8534 | 10.4128 | 10.4128 | 17.9353 | 17.9353 | 20.1976 | 20.1976 | 21.133 | 21.133 | 15.7207 | 15.7207 | 13.9509 | 13.9509 | 11.5985 | 11.5985 | 12.4603 | 12.4603 | 5.9981 | 5.9981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8022 | 4.8022 | 10.5311 | 10.5311 | 15.5345 | 15.5345 | 18.5887 | 18.5887 | 19.2246 | 19.2246 | 15.7223 | 15.7223 | 13.9007 | 13.9007 | 14.6253 | 14.6253 | 12.9738 | 12.9738 | 4.3662 | 4.3662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6667 | 3.6667 | 5.675 | 5.675 | 15.2715 | 15.2715 | 17.0823 | 17.0823 | 13.6881 | 13.6881 | 15.272 | 15.272 | 17.6471 | 17.6471 | 15.5195 | 15.5195 | 9.8034 | 9.8034 | 4.7712 | 4.7712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.618 | 4.618 | 8.9706 | 8.9706 | 9.5748 | 9.5748 | 9.6296 | 9.6296 | 15.127 | 15.127 | 8.0742 | 8.0742 | 13.6305 | 13.6305 | 8.227 | 8.227 | 6.6695 | 6.6695 | 2.4918 | 2.4918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.126 | 3.126 | 9.5035 | 9.5035 | 14.1593 | 14.1593 | 17.0798 | 17.0798 | 11.294 | 11.294 | 9.429 | 9.429 | 9.1187 | 9.1187 | 6.9765 | 6.9765 | 6.5578 | 6.5578 | 1.874 | 1.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8245 | 2.8245 | 5.2 | 5.2 | 6.1554 | 6.1554 | 8.0262 | 8.0262 | 12.4394 | 12.4394 | 12.535 | 12.535 | 13.0695 | 13.0695 | 6.7351 | 6.7351 | 5.697 | 5.697 | 2.4792 | 2.4792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3528 | 1.3528 | 6.3633 | 6.3633 | 7.6471 | 7.6471 | 14.6838 | 14.6838 | 19.0791 | 19.0791 | 14.467 | 14.467 | 11.94 | 11.94 | 7.8038 | 7.8038 | 4.7315 | 4.7315 | 2.112 | 2.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4554 | 2.4554 | 4.4668 | 4.4668 | 7.4482 | 7.4482 | 8.1612 | 8.1612 | 5.8638 | 5.8638 | 4.0672 | 4.0672 | 16.7002 | 16.7002 | 10.5075 | 10.5075 | 5.18 | 5.18 | 2.5868 | 2.5868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4013 | 1.4013 | 5.3013 | 5.3013 | 7.7836 | 7.7836 | 12.0206 | 12.0206 | 15.5436 | 15.5436 | 12.3907 | 12.3907 | 10.1982 | 10.1982 | 10.1445 | 10.1445 | 6.0038 | 6.0038 | 2.7476 | 2.7476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7508 | 1.7508 | 6.918 | 6.918 | 5.6285 | 5.6285 | 12.0669 | 12.0669 | 15.1915 | 15.1915 | 17.564 | 17.564 | 11.9085 | 11.9085 | 10.1496 | 10.1496 | 6.9488 | 6.9488 | 2.1751 | 2.1751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.528 | 1.528 | 5.2756 | 5.2756 | 7.5082 | 7.5082 | 11.9454 | 11.9454 | 15.9586 | 15.9586 | 17.5123 | 17.5123 | 20.8844 | 20.8844 | 16.2269 | 16.2269 | 12.9382 | 12.9382 | 4.1675 | 4.1675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8063 | 1.8063 | 4.7071 | 4.7071 | 10.8137 | 10.8137 | 9.8387 | 9.8387 | 17.5397 | 17.5397 | 12.01 | 12.01 | 14.5149 | 14.5149 | 10.865 | 10.865 | 7.9288 | 7.9288 | 2.7131 | 2.7131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9537 | 2.9537 | 7.9454 | 7.9454 | 9.0696 | 9.0696 | 12.9921 | 12.9921 | 18.5247 | 18.5247 | 17.5349 | 17.5349 | 11.5791 | 11.5791 | 8.7208 | 8.7208 | 8.5909 | 8.5909 | 1.8635 | 1.8635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4438 | 1.4438 | 7.6704 | 7.6704 | 10.7082 | 10.7082 | 11.7777 | 11.7777 | 13.2309 | 13.2309 | 12.3539 | 12.3539 | 10.4422 | 10.4422 | 9.3794 | 9.3794 | 5.1055 | 5.1055 | 2.1911 | 2.1911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83189 | 0.83189 | 3.0265 | 3.0265 | 7.2913 | 7.2913 | 8.1258 | 8.1258 | 11.3024 | 11.3024 | 11.7008 | 11.7008 | 10.9124 | 10.9124 | 6.3795 | 6.3795 | 5.4531 | 5.4531 | 0.90151 | 0.90151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18088 | 0.18088 | 2.2548 | 2.2548 | 10.4506 | 10.4506 | 10.5043 | 10.5043 | 17.8936 | 17.8936 | 23.4942 | 23.4942 | 19.3987 | 19.3987 | 16.4659 | 16.4659 | 13.5161 | 13.5161 | 8.0351 | 8.0351 | 1.095 | 1.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42437 | 0.42437 | 5.0197 | 5.0197 | 7.7405 | 7.7405 | 6.4064 | 6.4064 | 11.2776 | 11.2776 | 9.9053 | 9.9053 | 12.8737 | 12.8737 | 18.6219 | 18.6219 | 9.2978 | 9.2978 | 4.7111 | 4.7111 | 0.85153 | 0.85153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23836 | 0.23836 | 1.6313 | 1.6313 | 7.1394 | 7.1394 | 15.2514 | 15.2514 | 19.8567 | 19.8567 | 22.7972 | 22.7972 | 20.8932 | 20.8932 | 13.1065 | 13.1065 | 10.4761 | 10.4761 | 3.7446 | 3.7446 | 0.62801 | 0.62801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20734 | 0.20734 | 2.4419 | 2.4419 | 6.8415 | 6.8415 | 13.0235 | 13.0235 | 19.7738 | 19.7738 | 18.8018 | 18.8018 | 15.5329 | 15.5329 | 12.733 | 12.733 | 6.7319 | 6.7319 | 3.1441 | 3.1441 | 0.19933 | 0.19933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61503 | 0.61503 | 5.7379 | 5.7379 | 7.444 | 7.444 | 9.0977 | 9.0977 | 10.3755 | 10.3755 | 11.724 | 11.724 | 12.6896 | 12.6896 | 9.7674 | 9.7674 | 5.2389 | 5.2389 | 0.79978 | 0.79978 | 0.16174 | 0.16174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15146 | 0.15146 | 4.0107 | 4.0107 | 5.4764 | 5.4764 | 9.5387 | 9.5387 | 9.5316 | 9.5316 | 12.2891 | 12.2891 | 9.1697 | 9.1697 | 5.1099 | 5.1099 | 3.7715 | 3.7715 | 0.97518 | 0.97518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-10-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6225 | 2.6225 | 7.8654 | 7.8654 | 15.7801 | 15.7801 | 17.84 | 17.84 | 19.8353 | 19.8353 | 16.3554 | 16.3554 | 11.8555 | 11.8555 | 8.4008 | 8.4008 | 1.2933 | 1.2933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0859 | 4.0859 | 4.7814 | 4.7814 | 8.8611 | 8.8611 | 8.8994 | 8.8994 | 11.1139 | 11.1139 | 11.9973 | 11.9973 | 9.2396 | 9.2396 | 5.7077 | 5.7077 | 0.45092 | 0.45092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6206 | 8.6206 | 14.1253 | 14.1253 | 17.1209 | 17.1209 | 21.3324 | 21.3324 | 20.8654 | 20.8654 | 16.6414 | 16.6414 | 15.2862 | 15.2862 | 10.8079 | 10.8079 | 0.22327 | 0.22327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3538 | 6.3538 | 11.6568 | 11.6568 | 24.0109 | 24.0109 | 22.0037 | 22.0037 | 16.6445 | 16.6445 | 13.3092 | 13.3092 | 10.8523 | 10.8523 | 10.2121 | 10.2121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1269 | 4.1269 | 9.1422 | 9.1422 | 12.2237 | 12.2237 | 18.0281 | 18.0281 | 11.0519 | 11.0519 | 9.7925 | 9.7925 | 10.2631 | 10.2631 | 4.4673 | 4.4673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1566 | 5.1566 | 8.0298 | 8.0298 | 12.374 | 12.374 | 14.7256 | 14.7256 | 8.8278 | 8.8278 | 12.9335 | 12.9335 | 9.7689 | 9.7689 | 4.7165 | 4.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2325 | 7.2325 | 9.7036 | 9.7036 | 13.7164 | 13.7164 | 19.0724 | 19.0724 | 15.8058 | 15.8058 | 11.1123 | 11.1123 | 6.5514 | 6.5514 | 6.1684 | 6.1684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7197 | 3.7197 | 8.0612 | 8.0612 | 12.8256 | 12.8256 | 14.0976 | 14.0976 | 10.0377 | 10.0377 | 10.2806 | 10.2806 | 8.7944 | 8.7944 | 3.3746 | 3.3746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3587 | 5.3587 | 12.1897 | 12.1897 | 18.3499 | 18.3499 | 12.6212 | 12.6212 | 9.5306 | 9.5306 | 7.5273 | 7.5273 | 5.7944 | 5.7944 | 3.3541 | 3.3541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1462 | 3.1462 | 6.323 | 6.323 | 12.3812 | 12.3812 | 7.1082 | 7.1082 | 11.1688 | 11.1688 | 8.648 | 8.648 | 11.3604 | 11.3604 | 5.3719 | 5.3719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.606 | 6.606 | 9.3706 | 9.3706 | 14.0094 | 14.0094 | 15.7186 | 15.7186 | 13.8632 | 13.8632 | 13.5569 | 13.5569 | 8.7316 | 8.7316 | 4.1708 | 4.1708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1774 | 3.1774 | 8.991 | 8.991 | 13.2064 | 13.2064 | 15.1074 | 15.1074 | 14.4124 | 14.4124 | 12.914 | 12.914 | 7.7507 | 7.7507 | 5.289 | 5.289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6716 | 4.6716 | 9.6825 | 9.6825 | 14.933 | 14.933 | 14.8351 | 14.8351 | 14.3034 | 14.3034 | 11.6957 | 11.6957 | 6.9285 | 6.9285 | 6.5337 | 6.5337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.445 | 6.445 | 11.2023 | 11.2023 | 15.0009 | 15.0009 | 23.2946 | 23.2946 | 20.2375 | 20.2375 | 13.6217 | 13.6217 | 15.7873 | 15.7873 | 9.6528 | 9.6528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2716 | 2.2716 | 4.5439 | 4.5439 | 6.8572 | 6.8572 | 9.031 | 9.031 | 9.1771 | 9.1771 | 8.2045 | 8.2045 | 4.7293 | 4.7293 | 2.681 | 2.681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2263 | 3.2263 | 2.5365 | 2.5365 | 5.6721 | 5.6721 | 5.9818 | 5.9818 | 10.0296 | 10.0296 | 8.2688 | 8.2688 | 5.4517 | 5.4517 | 2.646 | 2.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3803 | 2.3803 | 4.1584 | 4.1584 | 12.7155 | 12.7155 | 10.9353 | 10.9353 | 15.9491 | 15.9491 | 8.9851 | 8.9851 | 5.64 | 5.64 | 3.8284 | 3.8284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1227 | 3.1227 | 10.4782 | 10.4782 | 11.3215 | 11.3215 | 15.4065 | 15.4065 | 18.3997 | 18.3997 | 12.7572 | 12.7572 | 8.5642 | 8.5642 | 6.2803 | 6.2803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2179 | 5.2179 | 10.4939 | 10.4939 | 16.7388 | 16.7388 | 17.1822 | 17.1822 | 17.1698 | 17.1698 | 11.9368 | 11.9368 | 8.7118 | 8.7118 | 3.5894 | 3.5894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6458 | 2.6458 | 7.8919 | 7.8919 | 10.6029 | 10.6029 | 11.4633 | 11.4633 | 13.6445 | 13.6445 | 8.6891 | 8.6891 | 11.6848 | 11.6848 | 5.1999 | 5.1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7532 | 1.7532 | 3.2688 | 3.2688 | 5.9677 | 5.9677 | 4.1815 | 4.1815 | 6.6471 | 6.6471 | 7.8054 | 7.8054 | 4.6888 | 4.6888 | 2.0831 | 2.0831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3532 | 1.3532 | 3.3666 | 3.3666 | 8.187 | 8.187 | 12.4701 | 12.4701 | 9.6454 | 9.6454 | 8.1466 | 8.1466 | 9.652 | 9.652 | 4.8821 | 4.8821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.678 | 2.678 | 7.3614 | 7.3614 | 15.5717 | 15.5717 | 20.2389 | 20.2389 | 15.6772 | 15.6772 | 14.8006 | 14.8006 | 9.2455 | 9.2455 | 5.5963 | 5.5963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3461 | 2.3461 | 5.1619 | 5.1619 | 13.3371 | 13.3371 | 16.628 | 16.628 | 15.0123 | 15.0123 | 11.4785 | 11.4785 | 7.3426 | 7.3426 | 5.54 | 5.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8201 | 1.8201 | 5.2967 | 5.2967 | 6.1353 | 6.1353 | 5.2925 | 5.2925 | 6.6745 | 6.6745 | 8.2739 | 8.2739 | 6.1665 | 6.1665 | 1.6126 | 1.6126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.379 | 2.379 | 6.5612 | 6.5612 | 10.2959 | 10.2959 | 12.5048 | 12.5048 | 14.6159 | 14.6159 | 13.3445 | 13.3445 | 8.7392 | 8.7392 | 2.8281 | 2.8281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3327 | 2.3327 | 8.6361 | 8.6361 | 12.3279 | 12.3279 | 15.9064 | 15.9064 | 11.483 | 11.483 | 8.2763 | 8.2763 | 5.7937 | 5.7937 | 3.2746 | 3.2746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93615 | 0.93615 | 4.1105 | 4.1105 | 7.0884 | 7.0884 | 8.486 | 8.486 | 6.9798 | 6.9798 | 6.1214 | 6.1214 | 3.3845 | 3.3845 | 3.8342 | 3.8342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4341 | 1.4341 | 6.3961 | 6.3961 | 13.7892 | 13.7892 | 11.482 | 11.482 | 12.533 | 12.533 | 11.2846 | 11.2846 | 8.1719 | 8.1719 | 3.3137 | 3.3137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94306 | 0.94306 | 4.1134 | 4.1134 | 7.3292 | 7.3292 | 9.2814 | 9.2814 | 8.9667 | 8.9667 | 8.0677 | 8.0677 | 5.8925 | 5.8925 | 2.3199 | 2.3199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-11-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2199 | 1.2199 | 7.7806 | 7.7806 | 13.4757 | 13.4757 | 13.3146 | 13.3146 | 13.4101 | 13.4101 | 9.8775 | 9.8775 | 5.8152 | 5.8152 | 3.3411 | 3.3411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40364 | 0.40364 | 7.2289 | 7.2289 | 8.4717 | 8.4717 | 10.9973 | 10.9973 | 14.9553 | 14.9553 | 15.1801 | 15.1801 | 10.981 | 10.981 | 3.4245 | 3.4245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1196 | 0.1196 | 1.8806 | 1.8806 | 5.3732 | 5.3732 | 7.3151 | 7.3151 | 10.5884 | 10.5884 | 8.5724 | 8.5724 | 5.7276 | 5.7276 | 2.784 | 2.784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3214 | 4.3214 | 6.5866 | 6.5866 | 4.0108 | 4.0108 | 9.1062 | 9.1062 | 4.4191 | 4.4191 | 3.4561 | 3.4561 | 1.6123 | 1.6123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.53 | 8.53 | 13.4239 | 13.4239 | 16.4595 | 16.4595 | 15.4093 | 15.4093 | 12.0005 | 12.0005 | 5.7491 | 5.7491 | 1.7256 | 1.7256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4272 | 6.4272 | 9.4772 | 9.4772 | 10.1267 | 10.1267 | 9.6728 | 9.6728 | 7.0905 | 7.0905 | 4.2433 | 4.2433 | 1.3741 | 1.3741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6058 | 2.6058 | 2.8627 | 2.8627 | 4.4196 | 4.4196 | 4.9487 | 4.9487 | 4.7984 | 4.7984 | 4.9398 | 4.9398 | 0.98689 | 0.98689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3872 | 2.3872 | 7.384 | 7.384 | 6.3496 | 6.3496 | 5.8746 | 5.8746 | 10.3259 | 10.3259 | 9.7772 | 9.7772 | 2.3216 | 2.3216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5545 | 6.5545 | 9.6338 | 9.6338 | 11.7378 | 11.7378 | 7.6404 | 7.6404 | 10.198 | 10.198 | 8.8605 | 8.8605 | 3.7986 | 3.7986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4158 | 6.4158 | 12.5277 | 12.5277 | 12.934 | 12.934 | 16.841 | 16.841 | 16.1569 | 16.1569 | 9.5291 | 9.5291 | 4.3464 | 4.3464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0438 | 1.0438 | 2.2534 | 2.2534 | 1.9216 | 1.9216 | 4.4119 | 4.4119 | 3.5681 | 3.5681 | 2.6917 | 2.6917 | 0.92587 | 0.92587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9012 | 5.9012 | 10.1514 | 10.1514 | 11.4442 | 11.4442 | 10.8947 | 10.8947 | 9.5153 | 9.5153 | 7.364 | 7.364 | 1.8209 | 1.8209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1061 | 4.1061 | 5.8402 | 5.8402 | 7.8628 | 7.8628 | 8.8121 | 8.8121 | 6.0417 | 6.0417 | 6.8709 | 6.8709 | 1.9126 | 1.9126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9206 | 2.9206 | 6.6468 | 6.6468 | 6.7987 | 6.7987 | 7.5949 | 7.5949 | 11.0676 | 11.0676 | 4.8042 | 4.8042 | 1.9246 | 1.9246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.229 | 6.229 | 11.5524 | 11.5524 | 8.7731 | 8.7731 | 14.2521 | 14.2521 | 11.7914 | 11.7914 | 5.4157 | 5.4157 | 3.6622 | 3.6622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7556 | 4.7556 | 8.2957 | 8.2957 | 10.2771 | 10.2771 | 9.5522 | 9.5522 | 7.0095 | 7.0095 | 6.9528 | 6.9528 | 2.0383 | 2.0383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.217 | 9.217 | 12.8578 | 12.8578 | 13.4959 | 13.4959 | 10.0911 | 10.0911 | 4.4502 | 4.4502 | 4.6383 | 4.6383 | 1.5095 | 1.5095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8092 | 5.8092 | 9.511 | 9.511 | 13.2886 | 13.2886 | 13.9877 | 13.9877 | 11.522 | 11.522 | 6.1508 | 6.1508 | 3.2966 | 3.2966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0037 | 3.0037 | 8.0379 | 8.0379 | 9.5537 | 9.5537 | 7.5766 | 7.5766 | 7.6544 | 7.6544 | 5.7343 | 5.7343 | 2.0577 | 2.0577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2166 | 5.2166 | 10.6902 | 10.6902 | 18.7553 | 18.7553 | 15.184 | 15.184 | 8.3243 | 8.3243 | 7.8024 | 7.8024 | 3.6528 | 3.6528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8449 | 8.8449 | 15.671 | 15.671 | 14.0762 | 14.0762 | 10.4383 | 10.4383 | 10.1662 | 10.1662 | 5.1494 | 5.1494 | 1.9549 | 1.9549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2856 | 2.2856 | 7.3842 | 7.3842 | 6.3637 | 6.3637 | 7.3273 | 7.3273 | 3.5999 | 3.5999 | 3.7122 | 3.7122 | 1.4131 | 1.4131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0804 | 5.0804 | 9.3027 | 9.3027 | 11.1384 | 11.1384 | 12.5957 | 12.5957 | 10.8608 | 10.8608 | 6.8746 | 6.8746 | 2.3139 | 2.3139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.526 | 4.526 | 5.7111 | 5.7111 | 6.9318 | 6.9318 | 6.8267 | 6.8267 | 5.1185 | 5.1185 | 6.9545 | 6.9545 | 1.4775 | 1.4775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4202 | 4.4202 | 7.763 | 7.763 | 10.7756 | 10.7756 | 9.644 | 9.644 | 8.1347 | 8.1347 | 6.2704 | 6.2704 | 2.3537 | 2.3537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8841 | 2.8841 | 3.7002 | 3.7002 | 4.8835 | 4.8835 | 5.9627 | 5.9627 | 7.8074 | 7.8074 | 5.4935 | 5.4935 | 1.7734 | 1.7734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4227 | 3.4227 | 10.1225 | 10.1225 | 11.0438 | 11.0438 | 11.6397 | 11.6397 | 8.9189 | 8.9189 | 7.4204 | 7.4204 | 2.2652 | 2.2652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8079 | 4.8079 | 7.7314 | 7.7314 | 13.3295 | 13.3295 | 12.5521 | 12.5521 | 13.0818 | 13.0818 | 11.7898 | 11.7898 | 3.169 | 3.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.499 | 4.499 | 9.0307 | 9.0307 | 13.3388 | 13.3388 | 17.3308 | 17.3308 | 19.0962 | 19.0962 | 13.1044 | 13.1044 | 3.691 | 3.691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7548 | 3.7548 | 8.3761 | 8.3761 | 12.1801 | 12.1801 | 13.0898 | 13.0898 | 14.1204 | 14.1204 | 7.8892 | 7.8892 | 3.7901 | 3.7901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3259 | 3.3259 | 6.1752 | 6.1752 | 7.8318 | 7.8318 | 5.2872 | 5.2872 | 5.4612 | 5.4612 | 5.3507 | 5.3507 | 3.3956 | 3.3956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6111 | 3.6111 | 8.4665 | 8.4665 | 6.52 | 6.52 | 6.1304 | 6.1304 | 6.1037 | 6.1037 | 5.6506 | 5.6506 | 2.454 | 2.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total by HH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3567 | 5.3567 | 169.6166 | 169.6166 | 791.7825 | 791.7825 | 2295.4008 | 2295.4008 | 4264.9497 | 4264.9497 | 5929.7266 | 5929.7266 | 6772.7669 | 6772.7669 | 7053.5749 | 7053.5749 | 6840.8595 | 6840.8595 | 6300.8332 | 6300.8332 | 5134.506 | 5134.506 | 3856.3551 | 3856.3551 | 2521.7504 | 2521.7504 | 1334.9038 | 1334.9038 | 472.4225 | 472.4225 | 102.6948 | 102.6948 | 0 | 0 | 0 | 0 | 0 | 0
Year total | 107695

## DNO LOOKUP (hidden)
DNO LOOKUP
DNO | Annual in-plane irradiation kWh/m2
(10) UKPN - Eastern England | 1267
(11) WPD - East Midlands | 1195
(12) UKPN - London | 1259
(13) SPEN - Merseyside, Cheshire, N. Shropshire & N. Wales | 1125
(14) WPD - West Midlands | 1187
(15) NPG - North East England | 1126
(16) ENW - North West England | 1020
(17) SSEN - North Scotland | 899
(18) SPEN - Central and Southern Scotland | 1004
(19) UKPN - South East England | 1308
(20) SSEN - Southern England | 1278
(21) WPD - South Wales | 1122
(22) WPD - South West England | 1285
(23) NPG - Yorkshire | 1186