## Overview
2025-01-01 | Appendix G Summary Sheet
Overview
The following tabs provide a summary of some of the information included in the Appendix F and G of our Bilateral Connection Agreements (BCAs) with the National Energy Sytem Operator (NESO).
The Bilateral Connection Agreement, or BCA, is a formal contract which one of UK Power Networks licence areas, Eastern Power Networks (EPN), London Power Networks (LPN) and South Eastern Power Networks (SPN), must hold with the NESO regarding the use and operation of any Grid Supply Point (GSP) in that licence area. Each GSP within our licence areas has a BCA in place with the NESO.
The Appendix G of the BCA contains the list of generators with a capacity equal or greater than 1 MW (and less than 100 MW) connected or accepted to connect to that GSP from the distribution network. In order to update the Appendix G in the BCA (due to new generation, cancellations or modifications), UK Power Networks applies for a variation of the BCA.
-> | When a generator applies for and accepts a connection offer issued by UK Power Networks, and it is connecting to a GSP with materiality headroom, UK Power Networks will include the generator in the monthly Appendix G submitted to the NESO.
-> | When a generator applies for and accepts a connection offer issued by UK Power Networks, and it is connecting to a GSP with no available materiality headroom, UK Power Networks will submit an application to vary the BCA.
UK Power Networks aims to submit the relevant application to NESO within 3 months (90 days) of the generator's acceptance (please see Flow diagram below).
Generators are included in the Appendix G based on their Acceptance Date, not Application Date. And the queue position for curtailment is based on the Application Date LIFO stack. Therefore, a project's Appendix G queue position and its Last in, First out (LIFO) stack queue position may not always align.
Some GSPs are awaiting the outcome of the Step 2 process, where an initial Step 1 BCA was issued with an indicative connection date, but with said date subject to changes in the definitive Step 2 BCA.
As part of UK Power Networks wider push throughout RIIO-ED2, we are providing key information contained in our BCA's to offer better visibility and support.
Flow diagram describing Appendix G / Project Progression process:

## Legend
| 2025-01-01 | Appendix G Summary Sheet
Legend
This document provides the summary for GSPs, differentiating between Mark 1 and Mark 2 Appendix G formats. A Mark 1 format contains generators divided in 4 Parts, while Mark 2 includes all generators listed in a single Part 1.
Mark 1 Appendix G of BCA | Part 1 | Part 2 | Part 3 | Part 4 | Part 5 Materiality Headroom | Generation Capacity | Total Aggregated Developer Capacity | Connection Asset Reverse Power Limits | Fault Level headroom
Appendix G definition | Historic connections (No additions to this section) | Connections subject to technical Site Specific Conditions (SCC) as detailed in Appendix F of the BCA (e.g. Reverse Power Flow Control Scheme requirement) | Subject to interim restrictions on availability in detailed Appendix D and subject to technical Site Specific Conditions (SCC) as detailed in Appendix F of the BCA | Generation that can only connect on completion of works as detailed in construction agreement and subject to technical conditions as detailed in Appendix F3 of the BCA | Available materiality headroom at the GSP. | Total generation from Part 1 to Part 4. | Total capacity considered for the latest BCA study. This figure cannot be changed or exceeded without submission of either a Modification Application, Project Progression or Statement of Works. | Export Asset Power Limit, usually under (N-1) conditions | Calculated Fault Level. When Fault Level Headroom falls below 1.0kA a study is required and a request/Application submitted to the NESO.
Source | Monthly Appendix G update | Monthly Appendix G update | Monthly Appendix G update | Monthly Appendix G update | Latest signed BCA offer | Monthly Appendix G update | Latest signed BCA offer | Latest signed BCA offer | Latest signed BCA offer
Mark 2 Appendix G of BCA | Total MW | Total Developer Capacity | Materiality Trigger | Connection Asset Reverse Power Limits | Fault Level headroom
Appendix G definition | Total generation under the GSP | MW Subject to Cancellation Charge in accordance with CUSC Section 15 User Commitment Methodology and Construction Works. | Subject to interim restrictions on availability in detailed Appendix D and subject to technical conditions as detailed in BCA and Appendix F | Export Asset Power Limit, usually under (N-1) conditions | Calculated Fault Level. When Fault Level Headroom falls below 1.0kA a study is required and a request/Application submitted to the NESO.
Source | Monthly Appendix G update | Latest signed BCA offer | Latest signed BCA offer | Latest signed BCA offer | Latest signed BCA offer
Project Progression | Date of Last Signed BCA containing App G | Last Project Progression submission | Clock start date | Earliest Connection Date (Completion of Transmission Works) | Cancellation Charges Apply
Definition | Related to the latest signed BCA due to Appendix G increase (does not include contracts due to ModApp and BEGAs) | When the last batch of recently accepted generators was submitted to the NESO. | Related to the last Project Progression submission, date it was clock started. | Related to the latest signed offer (including Step 1 offer), date of connection following completion of Transmission Works. | Related to the latest signed BCA due to Appendix G increase (does not include contracts due to ModApp and BEGAs).
Appendix F of BCA | 1. Emergency Instructions | 2. Voltage Regulation at the Grid Supply Point | 3. Transmission System to Active Network Management Scheme | 4. Operational Visibility and Commercial Control | 5. SGT Reverse Power Flow Control Scheme | 6. SGT Flexible Forward Power Flow Control Scheme | 7. Grid Supply Point Technical Limit Scheme
Definition | UK Power Networks to maintain a facility to be able to de-energise the generator upon an emergency instruction from the NESO. | Embedded Large and Embedded Medium Power Stations are required to satisfy the reactive capability and voltage control requirements of CC.6.3.2, CC.6.3.8 Grid Code. Small Embedded Power Stations shall have a reactive capability of between 0.95 Power Factor Lead to 0.95 Power Factor Lag at Rated MW Output. | Subject to the requirements of the Transmission System to Active Network Management Scheme, which could trip generators following a combination of outages at the transmission level. | Requirement for the NESO to have visibility and control over the Relevant Embedded Power Station, with necessary arrangements in place. | Scheme to protect the Supergrid Transformers (SGTs), sets up an export limit at the GSP. Generator to be managed by the Distributed Energy Resources Management System (DERMS), export may be curtailed if the limit is breached. | Scheme to protect the Supergrid Transformers (SGTs), sets up an import limit at the GSP. Generator to be managed by the Distributed Energy Resources Management System (DERMS), import may be curtailed if the limit is breached. | (Optional) Scheme that allows generators behind transmission works to connect ahead of completion date, subjected to pre-established limits which may result in a varying degree of curtailment.
Source | Latest signed BCA full offer due to Appendix G increase
The relevant SSC for each generator are locked in on the first BCA the customer appears on. Following the implementation of Technical Limits in the GSP, SSC 4 and 7 would be added but would not be a requirement if the generator does not opt-in Technical Limts.
Glossary:
App G: Appendix G (of Bilateral Connection Agreement)
BCA: Bilateral Connection Agreement
DERMS: Distributed Energy Resources Management System
EPN: Eastern Power Networks
GSP: Grid Supply Point
LIFO: Last in, First out
LPN: London Power Networks
NESO: National Energy System Operator
SPN: South Eastern Power Networks

## GSPs with Appendix G Mark1
|  | 2025-01-01 | Appendix G Summary Sheet
GSP Summary with Mark 1 Appendix G
Grid Supply Point | Licence Area | Part 1 | Part 2 | Part 3 | Part 4 | Part 5 Materiality Headroom | Generation Capacity | Total Aggregated Developer Capacity | Connection Asset Reverse Power Limits | Fault Level headroom | Date of Last Signed BCA containing App G | Last Project Progression submission | Clock start date | Earliest Connection Date (Completion of Transmission Works) | Cancellation Charges Apply | Emergency Instructions | Voltage Regulation at the Grid Supply Point | SGT Reverse Power Flow Control Scheme | SGT Flexible Forward Power Flow Control Scheme | Grid Supply Point Technical Limit Scheme
|  | [MW] | [MW] | [MW] | [MW] | [MW] | [MW] | [MW] | [MVA] | [kA]
Barking 132kV* | EPN | 0 | 28 | 0 | 0 | 0 | 28 | 28 | N/A | 1.47 |  | 2023-04-21 | 2023-05-19 | Able to connect | N/A | Y | Y | TBC* | TBC* | TBC
Barking West 33kV* | EPN | 0 | 1.16 | 0 | 0 | 0 | 1.16 | 1.16 | N/A | TBC |  | 2023-04-21 | 2023-10-16 | Able to connect | N/A | Y | Y | TBC* | TBC* | TBC
Biggleswade | EPN | 0 | 0 | 0 | 239.7 | 0 | 239.7 | 139.9 | TBC | 0 |  | 2024-04-25 | 2024-05-22 | 31/10/2032* | N/A | Y | Y | TBC* | TBC* | TBC
Sundon^ | EPN | 184.5 | 484.6 | 0 | 293.3 | 0 | 962.4 | 1036 | 480 | 0 | 2023-09-18 | 2024-10-30 | 2024-11-05 | 2031-10-31 | Y | Y | Y | Y | N | TBC
New GSP triggered at Sundon* | EPN |  |  |  | 395.7 | 0 | 395.7 | 390.7 | N/A | 0 |  |  |  | 2034-10-31 | Y | Y | Y | N | N | N
Tottenham | EPN | 94.7 | 73.1 | 0 | 0 | 46.9 | 167.8 | 214.7 | 420 | 3 | 2018-12-18 | Monthly update | Monthly update | Able to connect | N/A | Y | Y | N | N | TBC
Walpole^ | EPN | 493.9 | 37 |  | 655.8 | 0 | 1186.7 | 1292.3 | N/A | 0 | 2022-11-15 | 2025-01-14 | TBC | 31/10/2033* | Y | Y | Y | N | N | TBC
New GSP triggered at Walpole* | EPN |  |  |  | 1222.5 | 0 | 1222.5 | 1106.9 | N/A | TBC |  |  |  | 2034-10-31 | Y | Y | Y | N | N | N
West Thurrock | EPN | 21.5 | 0 | 0 | 49.9 | 0 | 71.4 | 71.4 | 100 | 3 | 2022-12-21 | Monthly update | Monthly update | N/A | N/A | Y | Y | N | N | TBC
Littlebrook (LPN) | LPN | 24.8 | 0 | 88.6 | 0 | 0 | 113.4 | 113.4 | N/A | 3 | 2024-10-17 | 2024-04-12 | 2024-04-26 | 04/14/2026 | N | Y | Y | N | N | N
Beddington | SPN | 73.4 | 60.1 | 0 | 0 | 46.94 | 133.5 | 180.44 | 480 | 2.47 | 2023-12-07 | Monthly update | Monthly update | Able to connect | N/A | Y | Y | N | N | TBC
Chessington | SPN | 1 | 130 | 0 | 0 | 0 | 131 | 131 | 240 | 3 | 2023-10-06 | 2023-01-24 | 2023-02-03 | N/A | N/A | Y | Y | N | N | TBC
Kingsnorth | SPN | 50.9 | 190.2 | 0 | 0 | 17.5 | 241.1 | 258.6 | 240 | 2.93 | 2020-04-16 | Monthly update | Monthly update | Able to connect | N/A | Y | Y | N | N | TBC
*Information contained in latest unsigned offer.
^Has triggered a new GSP.

## GSPs with Appendix G Mark2
|  | 2025-01-01 | Appendix G Summary Sheet
GSP Summary with Mark 2 Appendix G
Grid Supply Point | Licence Area | Total MW | Total Developer Capacity | Materiality Trigger | Connection Asset Reverse Power Limits | Connection Asset Forward Power Limits | Fault Level headroom | Date of Last Signed Agreement | Last Project Progression submission | Clock start date | Earliest Connection Date | Cancellation Charges Apply | Emergency Instructions | Voltage Regulation at the Grid Supply Point | Transmission System to Active Network Management Scheme | Operational Visibility and Commercial Control | SGT Reverse Power Flow Control Scheme | SGT Flexible Forward Power Flow Control Scheme | Grid Supply Point Technical Limit Scheme
|  | [MW] | [MW] | [MW] | [MVA] | [MVA] | [kA]
Amersham | EPN | 243.5 | 0 | 243.5 | N/A | N/A | 1.23 | 2022-09-30 | 2023-07-26 | 2023-08-25 | Able to connect | N/A | Y | Y | N | Y | N | N | Y
Braintree1 | EPN | 406.9 | 345.6* | 406.9* | 183* | N/A | 0* | 2023-09-18 | 2024-07-17 | 2024-08-15 | 31/10/2034* | Y | Y | Y | N | Y | N | N | Y
Bramford^ | EPN | 1771.6 | 887.8 | 2079.6 | 1046 | N/A | 0 | 2023-10-10 | 2024-10-31 | 2024-12-02 | 2031-10-31 | Y | Y | Y | N | Y | Y | N | Y
New GSP triggered at Bramford* | EPN | 1121.7 | 838.5 | 838.5 | N/A | N/A | TBC |  |  |  | 2034-10-31 | Y | Y | Y | N | N | N | N | N
Brimsdown^ | EPN | 70 | 43.5* | 71.02* | N/A | N/A | 0* |  | 2024-08-06 | 2024-09-04 | 31/10/2033* | N | Y | Y | N | Y | N | N | Y
New GSP triggered at Brimsdown* | EPN | 99.9 | 99.9 | 99.9 | N/A | N/A | TBC |  |  |  | 2033-10-31 | Y | Y | Y | N | N | N | N | N
Burwell | EPN | 1169.7 | 784.9* | 1119.6* | 3x 240* | 3x 240* | 0* | 2023-01-04 | 2025-01-05 | TBC | 31/10/2034* | Y | Y | Y | Y | Y | Y | Y | Y
Eaton Socon | EPN | 1176.7 | 925.6* | 1185.9* | 240* | N/A | 0* | 2023-06-26 | 2024-07-03 | 2024-07-17 | 31/10/2034* | Y | Y | Y | Y | Y | Y | N | Y
Elstree | EPN | 483.7 | 228.8* | 385.6* | N/A | N/A | 1.23* | 2017-09-26 | 2024-06-12 | 2024-06-28 | 31/10/2037* | Y | Y | Y | N | Y | N | Y | Y
Norwich Main^ | EPN | 1498 | 433.4 | 1498 | 720 | N/A | 0.92 | 2024-11-28 | 2024-09-17 | 2024-12-05 | 2032-10-31 | N | Y | Y | N | Y | Y | N | Y
New GSP triggered at Norwich Main* | EPN | 589.5 | 449.7 | 449.7 | TBC | N/A | TBC |  |  |  | 2034-10-31 | Y | Y | Y | N | N | N | N | N
Pelham2^ | EPN | 694 | N/A | 867.2 | 240 | N/A | 0.206 | 2023-07-28 | 2024-11-27 | 2025-01-13 | 2032-10-31 | Y | Y | Y | N | Y | Y | N | Y
New GSP triggered at Pelham* | EPN | 359.6 | 572.2 | 574.2 | 480 | N/A | TBC |  |  |  | 2034-10-31 | Y | Y | Y | N | N | Y | N | N
Rayleigh1 | EPN | 1398 | 1114.7* | 1418.7* | 606* | N/A | 0* | 2023-09-18 | 2024-12-18 | 2025-01-06 | 31/10/2034* | Y | Y | Y | N | Y | N | Y | Y
Rye House^ | EPN | 466.5 | 412.2* | 473* | N/A | N/A | 3* | 2022-12-15 | 2024-06-04 | 2024-07-02 | 31/10/2034* | Y | Y | Y | N | Y | N | N | Y
New GSP triggered at Rye House* | EPN | 219.8 | 249.7 | 249.7 | N/A | N/A | TBC |  |  |  | 2033-10-31 | Y | Y | Y | N | N | N | N | N
Tilbury | EPN | 492.74 | 532.4 | N/A | SGT1_7 240MVA / SGT2_8 240MVA | N/A | 3 | 2023-07-19 | 2023-03-14 | 2023-08-10 | 31/10/2033* | N | Y | Y | N | Y | N | N | Y
Warley | EPN | 735.3 | 644.8 | 971.9 | 460* | 460* | TBC* | 2022-05-27 | 2024-10-07 | 2024-10-16 | 31/10/2036* | Y | Y | Y | N | Y | Y | Y | Y
Watford South | EPN | 40 | 0 | 119.5 | 420 | N/A | 2.57 | 2017-09-26 | Monthly update | Monthly update | Able to connect | N/A | Y | Y | N | Y | N | N | Y
Wymondley2^ | EPN | 454.3 | 215 | 610.4 | 480 | N/A | 0.163 | 2023-07-28 | 2024-07-10 | 2024-07-29 | 31/10/2034* | Y | Y | Y | N | Y | Y | N | Y
New GSP triggered at Wymondley | EPN | 204.8 | 513.9 | 513.9 | 480 | N/A | TBC |  |  |  | 2034-10-31 | Y | Y | Y | N | N | Y | N | N
Bolney3^ | SPN | 1103.9 | 667.1 | 1261.6 | 1100 | N/A | 0 | 2023-07-14 | 2024-07-24 | 2024-08-02 | 2030-12-31 | Y | Y | Y | Y | Y | N | N | Y
New GSP triggered at Bolney* | SPN | 393.7 | 393.6 | 393.6 | 480 | 480 | TBC |  |  |  | 2037-10-31 | Y | Y | Y | Y | Y | N | N | N
Canterbury North3^ | SPN | 522.5 | 311.4* | 604.9* | 240* | 315* | 0* | 2023-03-20 | 2024-11-29 | 2024-12-17 | 01/06/2036* | N | Y | Y | Y | Y | Y | N | Y
New GSP triggered at Canterbury North* | SPN | 244.8 | 204.8 | 204.8 | N/A | N/A | 0 |  |  |  | 2036-06-01 | Y | Y | Y | Y | Y | N | N | N
Kemsley | SPN | 700.2 | 341.2* | 617.5* | 237* | 237* | 3* | 2021-11-02 | 2024-12-23 | TBC | 31/10/2036* | Y | Y | Y | N | Y | Y | N | Y
Little Horsted3 | SPN | 644.9 | 664.9* | 664.9* | 480* | 480* | 3* | 2023-10-20 | 2024-10-03 | 2024-10-16 | 31/10/2037* | Y | Y | Y | Y | Y | Y | Y | N/A
Ninfield3^ | SPN | 719.6 | 658.4* | 894.4* | 480* | N/A | 1.27* | 2023-09-11 | 2024-10-04 | 2024-10-16 | 31/10/2037* | Y* | Y | Y | Y | Y | N | Y | Y
New GSP triggered at Ninfield* | SPN | 98.5 | 49.9 | 49.9 | 240 | 240 | TBC |  |  |  | 2037-10-31 | Y | Y | Y | Y | Y | N | N | N
Northfleet East^ | SPN | 484.4 | N/A | 552.7 | 480 | N/A | 2.392 | 2022-04-16 | 2024-11-05 | 2024-11-20 | Able to connect | N/A | Y | Y | N | Y | N | N | Y
New GSP triggered at Northfleet East* | SPN | 906.4 | 757.3 | 757.3 | N/A | N/A | TBC |  |  |  | 2037-10-31 | N | Y | Y | N | N | N | N | N
Richborough3^ | SPN | 749.7 | 317.7* | 799.6* | 240* | N/A | 2.62* | 2023-03-13 | 2024-10-04 | 2024-11-26 | 31/10/2036* | N | Y | Y | Y | Y | Y | Y | Y
New GSP triggered at Richborough* | SPN | 212.1 | 97.2 | 97.2 | 240 | 240 | TBC |  |  |  | 30/11/2037* | Y | Y | Y | Y | Y | N | N | N
Sellindge3^ | SPN | 383.7 | 371.7* | 426.7* | 240* | N/A | 1.58* | 2023-07-12 | 2024-10-04 | TBC | 31/10/2036* | N | Y | Y | Y | Y | Y | Y | Y
New GSP triggered at Sellindge* | SPN | 104.9 | 49.9 | 49.9 | 240 | 240 | TBC |  |  |  | 2037-10-31 | Y | Y | Y | Y | Y | N | N | N
West Weybridge | SPN | 152.9 | 93.1* | 115.4* | 360* | 360* | 0* | 2018-05-09 | 2024-05-29 | 2024-06-21 | 30/10/2037* | Y | Y | Y | N | N | N | Y | N
1Project Progression raised together for Braintree and Rayleigh.
2Project Progression raised together for Pelham and Wymondley. Values are likely to change following the transfer of generation to Twinstead GSP.
3Project Progression raised together for Bolney, Canterbury, Little Horsted, Ninfield, Richborough and Sellindge as part of the SEC group.
*Information contained in latest unsigned offer.
^Has triggered a new GSP.